## Input Sheet -W'Gas
PROJECT INPUT SHEET: HBS SOLUTION | [18 empty] | 2026-03-02
Project Utility |  |  | Washington Gas |  |  |  | Project Name |  |  | Ohr Kodesh Congregation | [6 empty] | Project Type | Small | Building Tune-up
Square Footage |  |  |  |  | 46370 |  |  | (S.F.) | Annual Therm usage |  |  | 14200 |  |  | (Therm)
| No | Energy Conservation Method |  | Estimated Cost ($) | Natural Gas Savings (Therm/yr) | Natural Gas Energy Cost Savings ($/yr) | Simple Payback (years gas)
| 1 | Optimize HVAC Scheduling |  | 10500 | 6134.3224 | 7974.6191 | 1.3167
| 2 | AHU temperature scale adjustment |  | 5500 | 1143.874 | 1487.0362 | 3.6986
|  |  |  | Estimated Cost ($) | Natural Gas Savings (Therm/yr) | Electrical Energy Cost Savings ($/yr) | Simple Payback (years gas)
|  | Total Project Summary |  | 16000 | 7278.1964 | 9461.6553 | 1.691
|  | Total Project Summary (After Rebate) |  | 8000 | 7278.1964 | 9461.6553 | 0.84552
|  |  |  | Baseline (Therm) | Adjust (Therm) | % Decrease | Therm/SF |  | WG Incentive amount @ $3.7/Therm
|  |  |  | 14200 | 6921.8036 | 51.25% | 0.14927 |  | 8000
|  | Cooling Tonnage | EER (Existing) | EER (Proposed) | Cooling Eff (kW/Ton) | Heat Output (MBH) | Heating Efficiency | Supply Fan HP | Supply Fan Unit | Supply Fan Motor Load Factor | Supply Fan Motor Efficiency | Supply Fan Max CFM | Supply Fan Min CFM | Exhaust fans HP | Motor Efficiency | Number of Exhaust fans | Electric Heating
HVAC | AHU #1 | 39.1 | 10.5858 | 11.3 | 1.0619 | 469.2 | 85% | 20 | 1 | 0.65 | 0.88 | 15640 | 3910 |  | 0.9 |  | No
| AHU #2 | 61.6 | 10.5858 | 11.3 | 1.0619 | 739.2 | 85% | 20 | 1 | 0.65 | 0.88 | 24640 | 6160 |  | 0.9 |  | No
| AHU #3 | 66.5 | 10.5858 | 11.3 | 1.0619 | 798 | 85% | 20 | 1 | 0.65 | 0.88 | 26600 | 6650 |  | 0.9 |  | No
| AHU #4 | 17.6 | 10.5858 | 11.3 | 1.0619 | 211.2 | 85% | 5 | 1 | 0.65 | 0.88 | 7040 | 1760 |  | 0.9 |  | No
| AHU #5 | 2.6 | 10.5858 | 11.3 | 1.0619 | 31.2 | 85% | 0.75 | 1 | 0.65 | 0.88 | 1040 | 260 |  | 0.9 |  | No
| AHU #6 | 7.5 | 10.5858 | 11.3 | 1.0619 | 90 | 85% | 5 | 1 | 0.65 | 0.88 | 3000 | 750 |  | 0.9 |  | No
| AHU #7 | 3.4 | 10.5858 | 11.3 | 1.0619 | 40.8 | 85% | 1 | 1 | 0.65 | 0.88 | 1360 | 340 |  | 0.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 0.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 0.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 0.9 |  | No | EER Efficiency
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 0.9 |  | No | 0.0632
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 1.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 2.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 3.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 4.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 5.9 |  | No
| RTU # 1 | 15 | 9.368 | 10 | 1.2 | 180 | 85% | 1.5 | 1 | 0.65 | 0.88 | 6000 | 1500 |  | 6.9 |  | No
|  | 0 | 8.1502 | 8.7 | 1.3793 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 7.9 |  | No
|  | 0 | 8.1502 | 8.7 | 1.3793 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 8.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 9.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 10.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 11.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 12.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 13.9 |  | No
|  | 0 | 10.5858 | 11.3 | 1.0619 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 14.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 15.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 16.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 17.9 |  | No
|  | 0 | 10.4922 | 11.2 | 1.0714 | 0 | 85% | 0 | 1 | 0.65 | 0.88 | 0 | 0 |  | 18.9 |  | No
|  | Cooling Tonnage | EER (Existing) | EER (Proposed) | Cooling Eff (kW/Ton)
CHIILLER | CH 1 | 100 | 10.1174 | 10.8 | 1.1111
| CH 2 | 100 | 10.1174 | 10.8 | 1.1111
|  | MBH | EER (Proposed) | Cooling Eff (kW/Ton) | Fan Motor HP | Fan Motor kW
FREEZER | Walk-in 1 | 6.5 | 10 | 1.2 | 0.066667 | 0.049713
| Walk-in 2 | 6.5 | 10 | 1.2 | 0.066667 | 0.049713

## ECM1
ECM- |  |  |  | 1 | Optimize HVAC Scheduling
Input Variables | [5 empty] | Equations & Variables
Cost of Electricity ($/ kwh) |  |  | 0.12 |  |  | Cooling Savings (kWh) |  | =Tons*(12/EER)*Bin Hours
Cost of Natural Gas ($/ Therm) |  |  | 1.3 |  |  | Heating Savings (kWh) |  | =Heat Capacity*Bin Hours*Load%
AHU Equipment Values | AHU #1 | AHU #2 | AHU #3 | AHU #4 | AHU #5 | AHU #6 | AHU #7
Cooling Tonnage | 39.1 | 61.6 | 66.5 | 17.6 | 2.6 | 7.5 | 3.4
EER (Proposed) | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
Heating Capacity (MBH) | 469.2 | 739.2 | 798 | 211.2 | 31.2 | 90 | 40.8
Heating Efficiency | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
Supply Fan HP | 20 | 20 | 20 | 5 | 0.75 | 5 | 1
Supply Fan Units | 1 | 1 | 1 | 1 | 1 | 1 | 1
Exhaust Fans HP | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Exhasut Fans Units | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Electric Heat | No | No | No | No | No | No | No
Energy & Cost Savings
| Heating Savings (KWh) |  |  | Cost Savings ($)
AHU #1 | 3328.56 |  |  | 4327.128
AHU #2 | 0 |  |  | 0
AHU #3 | 2781.7341 |  |  | 3616.2544
AHU #4 | 0 |  |  | 0
AHU #5 | 10.4122 |  |  | 13.5359
AHU #6 | 0 |  |  | 0
AHU #7 | 13.616 |  |  | 17.7008
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
0 | 0 |  |  | 0
TOTAL | 6134.3224 |  |  | 7974.6191
Total Heating Savings
Cooling % |  |  |  |  | Therms | 6134.3224
Heating % |  |  |  |  | Dollars | 7974.6191
Implement Optimal Scheduling
| Heating & Cooling Bin Data TMY3 |  |  |  |  | AHU #1
AHU #1 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (Therms) | Proposed Heating (Therms) | Heating Therms Saved | Cooling kWh Saved
| 102.5 | 3 | 3 | 100% |  | 124.5664 | 124.5664 |  |  |  | 0
| 97.5 | 28 | 26 | 100% |  | 1162.6195 | 1079.5752 |  |  |  | 83.0442
| 92.5 | 72 | 67 | 88.24% |  | 2637.8761 | 2454.6903 |  |  |  | 183.1858
| 87.5 | 192 | 172 | 76.47% |  | 6096.4248 | 5461.3805 |  |  |  | 635.0442
| 82.5 | 420 | 354 | 64.71% |  | 11284.2478 | 9511.0088 |  |  |  | 1773.2389
| 77.5 | 649 | 419 | 52.94% |  | 14266.5133 | 9210.5841 |  |  |  | 5055.9292
| 72.5 | 819 | 303 | 41.18% |  | 14002.7257 | 5180.4956 |  |  |  | 8822.2301
| 67.5 | 873 | 292 | 29.41% |  | 10661.4159 | 3566.0177 |  |  |  | 7095.3982
| 62.5 | 782 | 301 | 17.65% |  | 5730.0531 | 2205.5575 |  |  |  | 3524.4956
| 57.5 | 768 | 313 | 5.882% |  | 1875.823 | 764.4956 |  |  |  | 1111.3274
| 52.5 | 795 | 300 | 3.333% |  |  |  | 146.28 | 55.2 | 91.08
| 47.5 | 551 | 210 | 10% |  |  |  | 304.152 | 115.92 | 188.232
| 42.5 | 858 | 290 | 16.67% |  |  |  | 789.36 | 266.8 | 522.56
| 37.5 | 651 | 195 | 23.33% |  |  |  | 838.488 | 251.16 | 587.328
| 32.5 | 476 | 164 | 30% |  |  |  | 788.256 | 271.584 | 516.672
| 27.5 | 283 | 80 | 36.67% |  |  |  | 572.792 | 161.92 | 410.872
| 22.5 | 277 | 95 | 43.33% |  |  |  | 662.584 | 227.24 | 435.344
| 17.5 | 178 | 52 | 50% |  |  |  | 491.28 | 143.52 | 347.76
| 12.5 | 71 | 13 | 56.67% |  |  |  | 222.088 | 40.664 | 181.424
| 7.5 | 9 | 0 | 63.33% |  |  |  | 31.464 | 0 | 31.464
| 2.5 | 4 | 1 | 70% |  |  |  | 15.456 | 3.864 | 11.592
| -2.5 | 1 | 0 | 76.67% |  |  |  | 4.232 | 0 | 4.232
|  | 8760 | 3650
[9 empty] | Totals | 3328.56 | 28283.8938
| Heating & Cooling Bin Data TMY3 |  |  |  |  | AHU #2
AHU #2 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (Therms) | Proposed Heating (Therms) | Heating Therms Saved | Cooling kWh Saved
| 102.5 | 2 | 2 | 100% |  | 130.8319 | 130.8319 |  |  |  | 0
| 97.5 | 2 | 2 | 100% |  | 130.8319 | 130.8319 |  |  |  | 0
| 92.5 | 6 | 6 | 88.24% |  | 346.3196 | 346.3196 |  |  |  | 0
| 87.5 | 20 | 20 | 76.47% |  | 1000.4789 | 1000.4789 |  |  |  | 0
| 82.5 | 37 | 37 | 64.71% |  | 1566.1343 | 1566.1343 |  |  |  | 0
| 77.5 | 20 | 20 | 52.94% |  | 692.6393 | 692.6393 |  |  |  | 0
| 72.5 | 23 | 23 | 41.18% |  | 619.5273 | 619.5273 |  |  |  | 0
| 67.5 | 14 | 14 | 29.41% |  | 269.3597 | 269.3597 |  |  |  | 0
| 62.5 | 15 | 15 | 17.65% |  | 173.1598 | 173.1598 |  |  |  | 0
| 57.5 | 30 | 30 | 5.882% |  | 115.4399 | 115.4399 |  |  |  | 0
| 52.5 | 21 | 21 | 3.333% |  |  |  | 6.0875 | 6.0875 | 0
| 47.5 | 24 | 24 | 10% |  |  |  | 20.8715 | 20.8715 | 0
| 42.5 | 11 | 11 | 16.67% |  |  |  | 15.9435 | 15.9435 | 0
| 37.5 | 11 | 11 | 23.33% |  |  |  | 22.3209 | 22.3209 | 0
| 32.5 | 3 | 3 | 30% |  |  |  | 7.8268 | 7.8268 | 0
| 27.5 | 10 | 10 | 36.67% |  |  |  | 31.8871 | 31.8871 | 0
| 22.5 | 6 | 6 | 43.33% |  |  |  | 22.6108 | 22.6108 | 0
| 17.5 | 5 | 5 | 50% |  |  |  | 21.7412 | 21.7412 | 0
| 12.5 | 0 | 0 | 56.67% |  |  |  | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% |  |  |  | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% |  |  |  | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% |  |  |  | 0 | 0 | 0
|  | 260 | 260
[9 empty] | Totals | 0 | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | AHU #3
AHU #3 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (Therms) | Proposed Heating (Therms) | Heating Therms Saved | Cooling kWh Saved
| 102.5 | 5 | 0 | 100% |  | 353.0973 | 0 |  |  |  | 353.0973
| 97.5 | 40 | 0 | 100% |  | 2824.7788 | 0 |  |  |  | 2824.7788
| 92.5 | 229 | 2 | 88.24% |  | 14269.2868 | 124.6226 |  |  |  | 14144.6642
| 87.5 | 435 | 11 | 76.47% |  | 23491.3587 | 594.0344 |  |  |  | 22897.3243
| 82.5 | 713 | 77 | 64.71% |  | 32580.4997 | 3518.5112 |  |  |  | 29061.9885
| 77.5 | 775 | 187 | 52.94% |  | 28974.7527 | 6991.3274 |  |  |  | 21983.4253
| 72.5 | 1091 | 211 | 41.18% |  | 31724.7579 | 6135.5856 |  |  |  | 25589.1723
| 67.5 | 1039 | 203 | 29.41% |  | 21580.4789 | 4216.3977 |  |  |  | 17364.0812
| 62.5 | 894 | 158 | 17.65% |  | 11141.2598 | 1969.037 |  |  |  | 9172.2228
| 57.5 | 759 | 153 | 5.882% |  | 3152.9516 | 635.5752 |  |  |  | 2517.3764
| 52.5 | 640 | 145 | 3.333% |  |  |  | 200.2824 | 45.3765 | 154.9059
| 47.5 | 671 | 206 | 10% |  |  |  | 629.9506 | 193.3976 | 436.5529
| 42.5 | 673 | 162 | 16.67% |  |  |  | 1053.0471 | 253.4824 | 799.5647
| 37.5 | 287 | 103 | 23.33% |  |  |  | 628.6988 | 225.6306 | 403.0682
| 32.5 | 196 | 79 | 30% |  |  |  | 552.0282 | 222.5012 | 329.5271
| 27.5 | 214 | 65 | 36.67% |  |  |  | 736.6635 | 223.7529 | 512.9106
| 22.5 | 83 | 39 | 43.33% |  |  |  | 337.6635 | 158.6612 | 179.0024
| 17.5 | 10 | 23 | 50% |  |  |  | 46.9412 | 107.9647 | -61.0235
| 12.5 | 5 | 1 | 56.67% |  |  |  | 26.6 | 5.32 | 21.28
| 7.5 | 1 | 0 | 63.33% |  |  |  | 5.9459 | 0 | 5.9459
| 2.5 | 0 | 0 | 70% |  |  |  | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% |  |  |  | 0 | 0 | 0
|  | 8760 | 1825
[9 empty] | Totals | 2781.7341 | 145908.1312
| Heating & Cooling Bin Data TMY3 |  |  |  |  | AHU #4
AHU #4 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (Therms) | Proposed Heating (Therms) | Heating Therms Saved | Cooling kWh Saved
| 102.5 | 5 | 5 | 100% |  | 93.4513 | 93.4513 |  |  |  | 0
| 97.5 | 40 | 40 | 100% |  | 747.6106 | 747.6106 |  |  |  | 0
| 92.5 | 229 | 229 | 88.24% |  | 3776.5331 | 3776.5331 |  |  |  | 0
| 87.5 | 435 | 435 | 76.47% |  | 6217.2618 | 6217.2618 |  |  |  | 0
| 82.5 | 713 | 713 | 64.71% |  | 8622.809 | 8622.809 |  |  |  | 0
| 77.5 | 775 | 775 | 52.94% |  | 7668.506 | 7668.506 |  |  |  | 0
| 72.5 | 1091 | 1091 | 41.18% |  | 8396.3269 | 8396.3269 |  |  |  | 0
| 67.5 | 1039 | 1039 | 29.41% |  | 5711.5252 | 5711.5252 |  |  |  | 0
| 62.5 | 894 | 894 | 17.65% |  | 2948.6642 | 2948.6642 |  |  |  | 0
| 57.5 | 759 | 759 | 5.882% |  | 834.4654 | 834.4654 |  |  |  | 0
| 52.5 | 640 | 640 | 3.333% |  |  |  | 53.0071 | 53.0071 | 0
| 47.5 | 671 | 671 | 10% |  |  |  | 166.7238 | 166.7238 | 0
| 42.5 | 673 | 673 | 16.67% |  |  |  | 278.7012 | 278.7012 | 0
| 37.5 | 287 | 287 | 23.33% |  |  |  | 166.3925 | 166.3925 | 0
| 32.5 | 196 | 196 | 30% |  |  |  | 146.1007 | 146.1007 | 0
| 27.5 | 214 | 214 | 36.67% |  |  |  | 194.9666 | 194.9666 | 0
| 22.5 | 83 | 83 | 43.33% |  |  |  | 89.3666 | 89.3666 | 0
| 17.5 | 10 | 10 | 50% |  |  |  | 12.4235 | 12.4235 | 0
| 12.5 | 5 | 5 | 56.67% |  |  |  | 7.04 | 7.04 | 0
| 7.5 | 1 | 1 | 63.33% |  |  |  | 1.5736 | 1.5736 | 0
| 2.5 | 0 | 0 | 70% |  |  |  | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% |  |  |  | 0 | 0 | 0
|  | 8760 | 8760
[9 empty] | Totals | 0 | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | AHU #5
AHU #5 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (Therms) | Proposed Heating (Therms) | Heating Therms Saved | Cooling kWh Saved
| 102.5 | 3 | 3 | 100% |  | 8.2832 | 8.2832 |  |  |  | 0
| 97.5 | 28 | 26 | 100% |  | 77.3097 | 71.7876 |  |  |  | 5.5221
| 92.5 | 70 | 67 | 88.24% |  | 170.5362 | 163.2275 |  |  |  | 7.3087
| 87.5 | 184 | 172 | 76.47% |  | 388.4977 | 363.1609 |  |  |  | 25.3368
| 82.5 | 384 | 356 | 64.71% |  | 686.0427 | 636.0187 |  |  |  | 50.0239
| 77.5 | 476 | 440 | 52.94% |  | 695.7876 | 643.165 |  |  |  | 52.6226
| 72.5 | 385 | 344 | 41.18% |  | 437.7095 | 391.0963 |  |  |  | 46.6132
| 67.5 | 364 | 325 | 29.41% |  | 295.596 | 263.925 |  |  |  | 31.671
| 62.5 | 354 | 334 | 17.65% |  | 172.4852 | 162.7402 |  |  |  | 9.7449
| 57.5 | 379 | 346 | 5.882% |  | 61.5554 | 56.1957 |  |  |  | 5.3597
| 52.5 | 369 | 337 | 3.333% |  |  |  | 4.5148 | 4.1233 | 0.39153
| 47.5 | 255 | 229 | 10% |  |  |  | 9.36 | 8.4056 | 0.95435
| 42.5 | 357 | 328 | 16.67% |  |  |  | 21.84 | 20.0659 | 1.7741
| 37.5 | 245 | 227 | 23.33% |  |  |  | 20.9835 | 19.4419 | 1.5416
| 32.5 | 214 | 193 | 30% |  |  |  | 23.5652 | 21.2527 | 2.3125
| 27.5 | 101 | 93 | 36.67% |  |  |  | 13.5934 | 12.5167 | 1.0767
| 22.5 | 118 | 108 | 43.33% |  |  |  | 18.7689 | 17.1784 | 1.5906
| 17.5 | 71 | 65 | 50% |  |  |  | 13.0306 | 11.9294 | 1.1012
| 12.5 | 19 | 18 | 56.67% |  |  |  | 3.952 | 3.744 | 0.208
| 7.5 | 2 | 2 | 63.33% |  |  |  | 0.46494 | 0.46494 | 0
| 2.5 | 0 | 1 | 70% |  |  |  | 0 | 0.25694 | -0.25694
| -2.5 | 0 | 1 | 76.67% |  |  |  | 0 | 0.28141 | -0.28141
|  | 4378 | 4015
[9 empty] | Totals | 10.4122 | 234.203
| Heating & Cooling Bin Data TMY3 |  |  |  |  | AHU #6
AHU #6 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (Therms) | Proposed Heating (Therms) | Heating Therms Saved | Cooling kWh Saved
| 102.5 | 3 | 3 | 100% |  | 23.8938 | 23.8938 |  |  |  | 0
| 97.5 | 5 | 5 | 100% |  | 39.823 | 39.823 |  |  |  | 0
| 92.5 | 20 | 20 | 88.24% |  | 140.5518 | 140.5518 |  |  |  | 0
| 87.5 | 39 | 39 | 76.47% |  | 237.5325 | 237.5325 |  |  |  | 0
| 82.5 | 48 | 48 | 64.71% |  | 247.3712 | 247.3712 |  |  |  | 0
| 77.5 | 41 | 41 | 52.94% |  | 172.8787 | 172.8787 |  |  |  | 0
| 72.5 | 30 | 30 | 41.18% |  | 98.3863 | 98.3863 |  |  |  | 0
| 67.5 | 21 | 21 | 29.41% |  | 49.1931 | 49.1931 |  |  |  | 0
| 62.5 | 39 | 39 | 17.65% |  | 54.8152 | 54.8152 |  |  |  | 0
| 57.5 | 42 | 42 | 5.882% |  |  |  | 2.6159 | 2.6159 | 0 | 0
| 52.5 | 23 | 23 | 3.333% |  |  |  | 0.81176 | 0.81176 | 0
| 47.5 | 37 | 37 | 10% |  |  |  | 3.9176 | 3.9176 | 0
| 42.5 | 18 | 18 | 16.67% |  |  |  | 3.1765 | 3.1765 | 0
| 37.5 | 14 | 14 | 23.33% |  |  |  | 3.4588 | 3.4588 | 0
| 32.5 | 6 | 6 | 30% |  |  |  | 1.9059 | 1.9059 | 0
| 27.5 | 16 | 16 | 36.67% |  |  |  | 6.2118 | 6.2118 | 0
| 22.5 | 9 | 9 | 43.33% |  |  |  | 4.1294 | 4.1294 | 0
| 17.5 | 5 | 5 | 50% |  |  |  | 2.6471 | 2.6471 | 0
| 12.5 | 0 | 0 | 56.67% |  |  |  | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% |  |  |  | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% |  |  |  | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% |  |  |  | 0 | 0 | 0
|  | 416 | 416
[9 empty] | Totals | 0 | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | AHU #7
AHU #7 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (Therms) | Proposed Heating (Therms) | Heating Therms Saved | Cooling kWh Saved
| 102.5 | 3 | 3 | 100% |  | 10.8319 | 10.8319 |  |  |  | 0
| 97.5 | 28 | 26 | 100% |  | 101.0973 | 93.8761 |  |  |  | 7.2212
| 92.5 | 70 | 67 | 88.24% |  | 223.0088 | 213.4513 |  |  |  | 9.5575
| 87.5 | 184 | 172 | 76.47% |  | 508.0354 | 474.9027 |  |  |  | 33.1327
| 82.5 | 384 | 356 | 64.71% |  | 897.1327 | 831.7168 |  |  |  | 65.4159
| 77.5 | 476 | 440 | 52.94% |  | 909.8761 | 841.0619 |  |  |  | 68.8142
| 72.5 | 385 | 344 | 41.18% |  | 572.3894 | 511.4336 |  |  |  | 60.9558
| 67.5 | 364 | 325 | 29.41% |  | 386.5487 | 345.1327 |  |  |  | 41.4159
| 62.5 | 354 | 334 | 17.65% |  | 225.5575 | 212.8142 |  |  |  | 12.7434
| 57.5 | 379 | 346 | 5.882% |  | 80.4956 | 73.4867 |  |  |  | 7.0088
| 52.5 | 369 | 337 | 3.333% |  |  |  | 5.904 | 5.392 | 0.512
| 47.5 | 255 | 229 | 10% |  |  |  | 12.24 | 10.992 | 1.248
| 42.5 | 357 | 328 | 16.67% |  |  |  | 28.56 | 26.24 | 2.32
| 37.5 | 245 | 227 | 23.33% |  |  |  | 27.44 | 25.424 | 2.016
| 32.5 | 214 | 193 | 30% |  |  |  | 30.816 | 27.792 | 3.024
| 27.5 | 101 | 93 | 36.67% |  |  |  | 17.776 | 16.368 | 1.408
| 22.5 | 118 | 108 | 43.33% |  |  |  | 24.544 | 22.464 | 2.08
| 17.5 | 71 | 65 | 50% |  |  |  | 17.04 | 15.6 | 1.44
| 12.5 | 19 | 18 | 56.67% |  |  |  | 5.168 | 4.896 | 0.272
| 7.5 | 2 | 2 | 63.33% |  |  |  | 0.608 | 0.608 | 0
| 2.5 | 0 | 1 | 70% |  |  |  | 0 | 0.336 | -0.336
| -2.5 | 0 | 1 | 76.67% |  |  |  | 0 | 0.368 | -0.368
|  | 4378 | 4015
[9 empty] | Totals | 13.616 | 306.2655
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 3 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 28 | 28 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 72 | 72 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 192 | 192 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 420 | 420 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 649 | 649 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 819 | 819 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 873 | 873 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 782 | 782 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 768 | 768 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 795 | 795 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 551 | 551 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 858 | 858 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 651 | 651 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 476 | 476 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 283 | 283 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 277 | 277 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 178 | 178 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 71 | 71 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 9 | 9 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 4 | 4 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 1 | 1 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 8760 | 8760
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 3 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 28 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 72 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 192 | 192 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 420 | 420 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 649 | 624 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 819 | 716 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 873 | 747 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 782 | 688 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 768 | 657 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 795 | 686 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 551 | 483 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 858 | 726 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 651 | 540 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 476 | 395 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 283 | 239 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 277 | 231 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 178 | 153 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 31 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 72 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 191 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 415 | 192 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 570 | 420 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 602 | 624 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 628 | 716 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 556 | 747 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 562 | 688 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 657 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 686 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 483 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 604 | 726 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 389 | 540 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 604 | 395 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 443 | 239 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 338 | 231 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 188 | 153 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 3 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 28 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 72 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 191 | 190 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 415 | 409 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 564 | 547 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 571 | 529 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 582 | 536 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 526 | 485 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 525 | 499 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 567 | 533 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 367 | 338 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 562 | 520 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 404 | 378 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 307 | 292 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 177 | 160 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 176 | 166 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 125 | 114 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 3 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 28 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 72 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 192 | 192 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 420 | 420 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 649 | 624 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 819 | 716 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 873 | 747 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 782 | 688 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 768 | 657 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 795 | 686 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 551 | 483 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 858 | 726 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 651 | 540 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 476 | 395 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 283 | 239 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 277 | 231 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 178 | 153 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 0 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 0 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 0 | 0 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 0 | 0 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 0 | 0 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 0 | 0 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 0 | 0 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 0 | 0 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 0 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 0 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 0 | 0 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 0 | 0 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 0 | 0 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 0 | 0 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 0 | 0 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 0 | 0 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF! | [5 empty] | Fan Motor Savings
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 0 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 0 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 0 | 0 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 0 | 0 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 0 | 0 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 0 | 0 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 0 | 0 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 0 | 0 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF! | [5 empty] | Fan Motor Savings
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 0 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 0 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 0 | 0 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 0 | 0 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 0 | 0 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 0 | 0 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 0 | 0 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 0 | 0 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF! | [5 empty] | Fan Motor Savings
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 0 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 0 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 0 | 0 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 0 | 0 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 0 | 0 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 0 | 0 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 0 | 0 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 0 | 0 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
|  | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF! | [5 empty] | Fan Motor Savings
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 0 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 0 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 0 | 0 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 0 | 0 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 0 | 0 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 0 | 0 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 0 | 0 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 0 | 0 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
|  | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.263% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 52.5 | 0 | 0 | 4.348% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 47.5 | 0 | 0 | 13.04% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 42.5 | 0 | 0 | 21.74% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 37.5 | 0 | 0 | 30.43% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 32.5 | 0 | 0 | 39.13% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 27.5 | 0 | 0 | 47.83% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 22.5 | 0 | 0 | 56.52% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| 17.5 | 0 | 0 | 65.22% |  |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | 0
| #REF! | #REF! | #REF! | #REF! |  |  |  | #DIV/0! | #DIV/0! |  |  | #REF! | #REF! | #REF!
|  | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | #REF!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0 | [5 empty] | Fan Motor Savings
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved | Existing Fan kWh | Proposed Fan kWh | Fan kWh Saved
| 102.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 97.5 | 0 | 0 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 92.5 | 0 | 0 | 88.24% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 87.5 | 0 | 0 | 76.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 82.5 | 0 | 0 | 64.71% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 77.5 | 0 | 0 | 52.94% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 72.5 | 0 | 0 | 41.18% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 67.5 | 0 | 0 | 29.41% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 62.5 | 0 | 0 | 17.65% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | 0 | 0 | 0
| 57.5 | 0 | 0 | 5.882% | [7 empty] | 0 | 0 | 0
| 52.5 | 0 | 0 | 3.333% | [7 empty] | 0 | 0 | 0
| 47.5 | 0 | 0 | 10% | [7 empty] | 0 | 0 | 0
| 42.5 | 0 | 0 | 16.67% | [7 empty] | 0 | 0 | 0
| 37.5 | 0 | 0 | 23.33% | [7 empty] | 0 | 0 | 0
| 32.5 | 0 | 0 | 30% | [7 empty] | 0 | 0 | 0
| 27.5 | 0 | 0 | 36.67% | [7 empty] | 0 | 0 | 0
| 22.5 | 0 | 0 | 43.33% | [7 empty] | 0 | 0 | 0
| 17.5 | 0 | 0 | 50% | [7 empty] | 0 | 0 | 0
| 12.5 | 0 | 0 | 56.67% | [7 empty] | 0 | 0 | 0
| 7.5 | 0 | 0 | 63.33% | [7 empty] | 0 | 0 | 0
| 2.5 | 0 | 0 | 70% | [7 empty] | 0 | 0 | 0
| -2.5 | 0 | 0 | 76.67% | [7 empty] | 0 | 0 | 0
|  | 0 | 0
[9 empty] | Totals | 0 | #DIV/0! |  | TOTALS | 0

## TMY3 DATA (Schedule - AHU) (hidden)
SCHEDULE
|  | EXISTING | [23 empty] | PROPOSED
|  | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | [9 empty] | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | RTU Equivalent Full Load Hours (%) at Each Bin | RTU Equivalent Full Load Hours (%) at Each Bin (PROPOSED)
|  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | EXISTING HVAC SCHEDULE | [31 empty] | EXISTING BIN HOURS | [39 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | [9 empty] | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Percent % | Percent % | [72 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2
102.5 | 100 to 105 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 31 | 3 | 3 | [9 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 100% | 0% | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3
97.5 | 95 to 100 | 28 | 28 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 16 | 28 | 72 | 28 | 28 | [9 empty] | 28 | 28 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 16 | 28 | 28 | 28 | 28 | 89.47% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 7:00 | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 700 | 0 | 0 | 0 | 0 | 0 | 0 | Start | [15 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4
92.5 | 90 to 95 | 72 | 72 | 68 | 68 | 68 | 72 | 72 | 72 | 72 | 72 | 19 | 72 | 191 | 72 | 72 | [9 empty] | 72 | 72 | 68 | 68 | 68 | 72 | 72 | 72 | 72 | 72 | 19 | 72 | 72 | 72 | 72 | 78.95% | 0% | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 14:00 | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | 1300 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | [15 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5
87.5 | 85 to 90 | 192 | 192 | 175 | 175 | 175 | 192 | 192 | 192 | 192 | 192 | 86 | 192 | 415 | 191 | 192 | [9 empty] | 192 | 192 | 175 | 175 | 175 | 192 | 192 | 191 | 192 | 192 | 86 | 192 | 192 | 190 | 192 | 68.42% | 0% | [72 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6
82.5 | 80 to 85 | 420 | 420 | 373 | 373 | 373 | 420 | 420 | 417 | 420 | 420 | 184 | 420 | 570 | 415 | 420 | [9 empty] | 420 | 420 | 373 | 373 | 373 | 420 | 420 | 415 | 420 | 420 | 183 | 420 | 420 | 409 | 420 | 57.89% | 0% | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7
77.5 | 75 to 80 | 649 | 649 | 513 | 513 | 513 | 649 | 649 | 577 | 649 | 649 | 256 | 649 | 602 | 564 | 649 | [9 empty] | 624 | 624 | 493 | 493 | 493 | 624 | 624 | 561 | 624 | 624 | 231 | 624 | 624 | 547 | 624 | 47.37% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | [15 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8
72.5 | 70 to 75 | 819 | 819 | 502 | 502 | 502 | 819 | 819 | 577 | 819 | 819 | 350 | 819 | 628 | 571 | 819 | [9 empty] | 716 | 716 | 445 | 445 | 445 | 716 | 716 | 538 | 716 | 716 | 276 | 716 | 716 | 529 | 716 | 36.84% | 0% | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 23:00 | 23:00 | 23:00 | 23:00 | 23:00 | 23:00 | 23:00 | Stop | 22:00 | 22:00 | 22:00 | 22:00 | 22:00 | 22:00 | 22:00 | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | Stop | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | Stop | [15 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
67.5 | 65 to 70 | 873 | 873 | 498 | 498 | 498 | 873 | 873 | 582 | 873 | 873 | 375 | 873 | 556 | 582 | 873 | [9 empty] | 747 | 747 | 433 | 433 | 433 | 747 | 747 | 541 | 747 | 747 | 287 | 747 | 747 | 536 | 747 | 26.32% | 0% | [72 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
62.5 | 60 to 65 | 782 | 782 | 473 | 473 | 473 | 782 | 782 | 537 | 782 | 782 | 292 | 782 | 562 | 526 | 782 | [9 empty] | 688 | 688 | 418 | 418 | 418 | 688 | 688 | 492 | 688 | 688 | 219 | 688 | 688 | 485 | 688 | 15.79% | 0% | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 11 | 11 | 11 | 11 | 11 | 11 | 11
57.5 | 55 to 60 | 768 | 768 | 467 | 467 | 467 | 768 | 768 | 521 | 768 | 768 | 322 | 768 | 0 | 525 | 768 | [9 empty] | 657 | 657 | 421 | 421 | 421 | 657 | 657 | 492 | 657 | 657 | 258 | 657 | 657 | 499 | 657 | 5.263% | 0% | Start | 12:00 AM | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 600 | 600 | 600 | 600 | 600 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | [7 empty] | Start | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 12 | 12 | 12 | 12 | 12 | 12 | 12
52.5 | 50 to 55 | 795 | 795 | 496 | 496 | 496 | 795 | 795 | 556 | 795 | 795 | 354 | 795 | 0 | 567 | 795 | [9 empty] | 686 | 686 | 431 | 431 | 431 | 686 | 686 | 526 | 686 | 686 | 278 | 686 | 686 | 533 | 686 | 4.348% | 0% | Stop | 12:00 AM | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 12:00 AM | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 2400 | 1700 | 1700 | 1700 | 1700 | 1700 | 2400 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | [7 empty] | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 13 | 13 | 13 | 13 | 13 | 13 | 13
47.5 | 45 to 50 | 551 | 551 | 333 | 333 | 333 | 551 | 551 | 374 | 551 | 551 | 239 | 551 | 0 | 367 | 551 | [9 empty] | 483 | 483 | 283 | 283 | 283 | 483 | 483 | 348 | 483 | 483 | 183 | 483 | 483 | 338 | 483 | 13.04% | 0% | [72 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
42.5 | 40 to 45 | 858 | 858 | 534 | 534 | 534 | 858 | 858 | 562 | 858 | 858 | 382 | 858 | 604 | 562 | 858 | [9 empty] | 726 | 726 | 466 | 466 | 466 | 726 | 726 | 515 | 726 | 726 | 290 | 726 | 726 | 520 | 726 | 21.74% | 0% | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 15 | 15 | 15 | 15 | 15 | 15 | 15
37.5 | 35 to 40 | 651 | 651 | 389 | 389 | 389 | 651 | 651 | 391 | 651 | 651 | 300 | 651 | 389 | 404 | 651 | [9 empty] | 540 | 540 | 322 | 322 | 322 | 540 | 540 | 361 | 540 | 540 | 218 | 540 | 540 | 378 | 540 | 30.43% | 0% | Start | 12:00 AM | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 600 | 600 | 600 | 600 | 600 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | [7 empty] | Start | [7 empty] | Start | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 16 | 16 | 16 | 16 | 16 | 16 | 16
32.5 | 30 to 35 | 476 | 476 | 291 | 291 | 291 | 476 | 476 | 303 | 476 | 476 | 179 | 476 | 604 | 307 | 476 | [9 empty] | 395 | 395 | 238 | 238 | 238 | 395 | 395 | 285 | 395 | 395 | 132 | 395 | 395 | 292 | 395 | 39.13% | 0% | Stop | 12:00 AM | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 12:00 AM | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 2400 | 1700 | 1700 | 1700 | 1700 | 1700 | 2400 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | [7 empty] | Stop | [7 empty] | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 17 | 17 | 17 | 17 | 17 | 17 | 17
27.5 | 25 to 30 | 283 | 283 | 157 | 157 | 157 | 283 | 283 | 178 | 283 | 283 | 118 | 283 | 443 | 177 | 283 | [9 empty] | 239 | 239 | 131 | 131 | 131 | 239 | 239 | 163 | 239 | 239 | 84 | 239 | 239 | 160 | 239 | 47.83% | 0% | [72 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
22.5 | 20 to 25 | 277 | 277 | 170 | 170 | 170 | 277 | 277 | 174 | 277 | 277 | 152 | 277 | 338 | 176 | 277 | [9 empty] | 231 | 231 | 147 | 147 | 147 | 231 | 231 | 161 | 231 | 231 | 115 | 231 | 231 | 166 | 231 | 56.52% | 0% | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
17.5 | 15 to 20 | 178 | 178 | 104 | 104 | 104 | 178 | 178 | 120 | 178 | 178 | 87 | 178 | 188 | 125 | 178 | [9 empty] | 153 | 153 | 92 | 92 | 92 | 153 | 153 | 112 | 153 | 153 | 70 | 153 | 153 | 114 | 153 | 65.22% | 0% | Start | 12:00 AM | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 600 | 600 | 600 | 600 | 600 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | [7 empty] | Start | [15 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
12.5 | 10 to 15 | 71 | 71 | 57 | 57 | 57 | 71 | 71 | 36 | 71 | 71 | 46 | 71 | 191 | 36 | 71 | [9 empty] | 57 | 57 | 39 | 39 | 39 | 57 | 57 | 31 | 57 | 57 | 31 | 57 | 57 | 34 | 57 | 73.91% | 0% | Stop | 12:00 AM | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 12:00 AM | Stop | 12:00 AM | 1:00 | 1:00 | 1:00 | 1:00 | 12:00 AM | 12:00 AM | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 2400 | 1700 | 1700 | 1700 | 1700 | 1700 | 2400 | Stop | 2400 | 0 | 0 | 0 | 0 | 2400 | 2400 | Stop | [7 empty] | Stop | [15 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
7.5 | 5 to 10 | 9 | 9 | 7 | 7 | 7 | 9 | 9 | 2 | 9 | 9 | 5 | 9 | 136 | 4 | 9 | [9 empty] | 5 | 5 | 2 | 2 | 2 | 5 | 5 | 2 | 5 | 5 | 1 | 5 | 5 | 4 | 5 | 82.61% | 0% | [72 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
2.5 | 0 to 5 | 4 | 4 | 2 | 2 | 2 | 4 | 4 | 2 | 4 | 4 | 2 | 4 | 41 | 2 | 4 | [9 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 91.3% | 0% | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
-2.5 | -5 to 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 1 | 1 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | [7 empty] | Start | [15 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | 8760 | 8760 | 5640 | 5640 | 5640 | 8760 | 8760 | 6204 | 8760 | 8760 | 3768 | 8760 | 6570 | 6205 | 8760 | [9 empty] | 7664 | 7664 | 5009 | 5009 | 5009 | 7664 | 7664 | 5839 | 7664 | 7664 | 2982 | 7664 | 7664 | 5839 | 7664 |  |  | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | [7 empty] | Stop
|  | 8760 | 8760 | 5640 | 5640 | 5640 | 8760 | 8760 | 6204 | 8760 | 8760 | 3768 | 8760 | 6570 | 6205 | 8760 | [9 empty] | 7664 | 7664 | 5009 | 5009 | 5009 | 7664 | 7664 | 5839 | 7664 | 7664 | 2982 | 7664 | 7664 | 5839 | 7664
|  | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | [9 empty] | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES |  |  | PROPOSED HVAC SCHEDULE | [31 empty] | PROPOSED BIN HOURS
RTU Load Profile |  |  |  | RTU Load Profile (Proposed) | [38 empty] | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
OAT | EFLCH % | EFLHH % |  | OAT | EFLCH % | EFLHH % | [36 empty] | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 7:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 700 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600
102.5 | 100% |  |  | 97.5 | 0% | [37 empty] | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 14:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 23:00 | 23:00 | 23:00 | 23:00 | 23:00 | 23:00 | 23:00 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 1300 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200
55 | 0% |  |  | 55 | 0%
55 |  | 0% |  | 55 |  | 0% |  |  |  | Reduction In Operating Hours | [32 empty] | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
-2.5 |  | 100% |  | 7.5 |  | 0% |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600
Slope | 0.021053 | -0.017391 |  | Slope | 0 | 0 |  |  |  | 1096 | 1096 | 631 | 631 | 631 | 1096 | 1096 | 365 | 1096 | 1096 | 786 | 1096 | -1094 | 366 | 1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 22:00 | 22:00 | 22:00 | 22:00 | 22:00 | 22:00 | 22:00 | Stop | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | Stop | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | Stop | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | Stop | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Intercept | -1.1579 | 0.95652 |  | Intercept | 0 | 0
[43 empty] | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
[43 empty] | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 6:00 | 9:00 | 6:00 | 9:00 | 6:00 | 6:00 | 6:00 | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 600 | 900 | 600 | 900 | 600 | 600 | 600
Conventional Binning :Conventional Bins for BALTIMORE BLT-WASHNGTN INT'L MD USFA #: 724060TY | [42 empty] | Stop | 1:00AM | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 1:00AM | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 0:00 | 18:00 | 23:00 | 18:00 | 23:00 | 0:00 | 0:00 | Stop | 2300 | 1700 | 1700 | 1700 | 1700 | 1700 | 2300 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 2300 | 1700 | 2200 | 1700 | 2200 | 2300 | 2300
BALTIMORE BLT-WASHNGTN INT'L, MD; USAF#: 724060TY; Altitude: 45 meters / 148 ft; Latitude: 39.167; Longitude: -76.683
Units: | I-P | 724060TY | BALTIMORE BLT-WASHNGTN INT'L, MD |  |  | 39.167 | -76.683 | 147.6378 ft | [34 empty] | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
[43 empty] | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | [7 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 | Start | 300 | 300 | 300 | 300 | 300 | 300 | 300
#REF! | [42 empty] | Stop | 1:00AM | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 1:00AM | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | Stop | 2300 | 1700 | 1700 | 1700 | 1700 | 1700 | 2300 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | [7 empty] | Stop | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [22 empty] | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [16 empty] | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 5:00 |  |  |  |  | 5:00 | 5:00 | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 | Start | 500 | 0 | 0 | 0 | 0 | 500 | 500 | Start | [7 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 | Start | 300 | 300 | 300 | 300 | 300 | 300 | 300
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [16 empty] | Stop | 1:00AM | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 1:00AM | Stop | 0:00 |  |  |  |  | 0:00 | 0:00 | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | Stop | 2300 | 1700 | 1700 | 1700 | 1700 | 1700 | 2300 | Stop | 2300 | 0 | 0 | 0 | 0 | 2300 | 2300 | Stop | [7 empty] | Stop | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500 | [23 empty] | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500 | [23 empty] | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | 5:00 | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | 6:00 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | 500 | 500 | 500 | 500 | 500 | 500 | 500 | Start | [7 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [16 empty] | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 0:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 0:00 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | [7 empty] | Stop | 2300 | 2000 | 2000 | 2000 | 2000 | 2000 | 2300
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 0 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 0 | 2400 | 2500
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 0 | 2400 | 2500
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 0 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | [5 empty] | 1 | [5 empty] | Sunday | 600 | 2400 | 2400
Monday | 600 | 1800 | 2500 | 2 | [5 empty] | 2 | [5 empty] | Monday | 600 | 1800 | 2400
Tuesday | 600 | 1800 | 2500 | 3 | [5 empty] | 3 | [5 empty] | Tuesday | 600 | 1800 | 2400
Wednesday | 600 | 1800 | 2500 | 4 | [5 empty] | 4 | [5 empty] | Wednesday | 600 | 1800 | 2400
Thursday | 600 | 1800 | 2500 | 5 | [5 empty] | 5 | [5 empty] | Thursday | 600 | 1800 | 2400
Friday | 600 | 1800 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 600 | 1800 | 2400 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 2600 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 600 | 2400 | 2400 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 600 | 2400 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 600 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 600 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 600 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 600 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 600 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 600 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 600 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 600 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 600 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 600 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | [5 empty] | 18 | [6 empty] | 600 | 2400 |  | 18 | [5 empty] | 18
|  |  |  | 19 | [5 empty] | 19 | [9 empty] | 19 | [5 empty] | 19
|  |  |  | 20 | [5 empty] | 20 | [9 empty] | 20 | [5 empty] | 20
|  |  |  | 21 | [5 empty] | 21 | [9 empty] | 21 | [5 empty] | 21
|  |  |  | 22 | [5 empty] | 22 | [9 empty] | 22 | [5 empty] | 22
|  |  |  | 23 | [5 empty] | 23 | [9 empty] | 23 | [5 empty] | 23
|  |  |  | 24 | [5 empty] | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 27 | [5 empty] | 8 | 19 | [6 empty] | 97.5 | 95 to 100 | 27 | [5 empty] | 8 | 19
92.5 | 90 to 95 | 68 | [5 empty] | 31 | 35 | 2 | [5 empty] | 92.5 | 90 to 95 | 68 | [5 empty] | 31 | 35 | 2
87.5 | 85 to 90 | 175 |  |  |  |  | 6 | 67 | 58 | 32 | 12 |  |  |  |  | 87.5 | 85 to 90 | 175 |  |  |  |  | 6 | 67 | 58 | 32 | 12
82.5 | 80 to 85 | 373 |  |  |  |  | 45 | 87 | 98 | 81 | 38 | 24 |  |  |  | 82.5 | 80 to 85 | 373 |  |  |  |  | 45 | 87 | 98 | 81 | 38 | 24
77.5 | 75 to 80 | 513 |  |  |  | 8 | 60 | 83 | 102 | 107 | 86 | 56 |  | 11 |  | 77.5 | 75 to 80 | 493 |  |  |  | 8 | 60 | 79 | 89 | 104 | 86 | 56 |  | 11
72.5 | 70 to 75 | 502 |  | 4 |  | 13 | 53 | 75 | 97 | 133 | 81 | 36 |  | 10 |  | 72.5 | 70 to 75 | 445 |  | 4 |  | 13 | 50 | 62 | 76 | 117 | 77 | 36 |  | 10
67.5 | 65 to 70 | 498 | 16 | 10 | 5 | 38 | 73 | 48 | 69 | 65 | 113 | 36 | 7 | 18 |  | 67.5 | 65 to 70 | 433 | 13 | 10 | 5 | 38 | 70 | 43 | 50 | 50 | 93 | 36 | 7 | 18
62.5 | 60 to 65 | 473 | 14 | 25 | 11 | 77 | 84 | 28 | 11 | 28 | 74 | 62 | 32 | 27 |  | 62.5 | 60 to 65 | 418 | 13 | 25 | 11 | 77 | 70 | 20 | 4 | 20 | 59 | 60 | 32 | 27
57.5 | 55 to 60 | 467 | 13 | 37 | 23 | 96 | 68 | 10 |  | 13 | 46 | 90 | 52 | 19 |  | 57.5 | 55 to 60 | 421 | 12 | 33 | 23 | 96 | 61 | 6 |  | 10 | 32 | 78 | 52 | 18
52.5 | 50 to 55 | 496 | 15 | 63 | 51 | 70 | 45 | 16 |  | 7 | 13 | 72 | 95 | 49 |  | 52.5 | 50 to 55 | 431 | 14 | 54 | 51 | 66 | 38 | 5 |  | 4 | 13 | 58 | 79 | 49
47.5 | 45 to 50 | 333 | 33 | 39 | 61 | 61 | 15 | 2 |  |  | 4 | 35 | 41 | 42 |  | 47.5 | 45 to 50 | 283 | 31 | 35 | 60 | 42 | 12 |  |  |  | 3 | 30 | 34 | 36
42.5 | 40 to 45 | 534 | 80 | 34 | 136 | 72 | 15 | 1 |  |  | 1 | 29 | 70 | 96 |  | 42.5 | 40 to 45 | 466 | 72 | 34 | 124 | 51 | 8 |  |  |  | 1 | 25 | 66 | 85
37.5 | 35 to 40 | 389 | 64 | 36 | 76 | 34 | 4 |  |  |  |  | 24 | 79 | 72 |  | 37.5 | 35 to 40 | 322 | 56 | 33 | 64 | 20 | [5 empty] | 14 | 73 | 62
32.5 | 30 to 35 | 291 | 57 | 46 | 73 | 10 | [5 empty] | 12 | 48 | 45 |  | 32.5 | 30 to 35 | 238 | 54 | 42 | 57 | 8 | [5 empty] | 6 | 39 | 32
27.5 | 25 to 30 | 157 | 35 | 51 | 19 | 1 | [5 empty] | 4 | 21 | 26 |  | 27.5 | 25 to 30 | 131 | 28 | 43 | 16 | 1 | [5 empty] | 3 | 15 | 25
22.5 | 20 to 25 | 170 | 69 | 26 | 9 | [7 empty] | 9 | 57 |  | 22.5 | 20 to 25 | 147 | 66 | 22 | 7 | [7 empty] | 9 | 43
17.5 | 15 to 20 | 104 | 49 | 31 | 4 | [7 empty] | 2 | 18 |  | 17.5 | 15 to 20 | 92 | 47 | 27 | 2 | [7 empty] | 2 | 14
12.5 | 10 to 15 | 57 | 34 | 21 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 39 | 19 | 18 | [9 empty] | 2
7.5 | 5 to 10 | 7 | 1 | 6 | [11 empty] | 7.5 | 5 to 10 | 2 | 1 | 1
2.5 | 0 to 5 | 2 |  | 2 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 5640 | [15 empty] | 5009
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | [5 empty] | 1 | [5 empty] | Sunday | 600 | 2400 | 2400
Monday | 600 | 1800 | 2500 | 2 | [5 empty] | 2 | [5 empty] | Monday | 600 | 1800 | 2400
Tuesday | 600 | 1800 | 2500 | 3 | [5 empty] | 3 | [5 empty] | Tuesday | 600 | 1800 | 2400
Wednesday | 600 | 1800 | 2500 | 4 | [5 empty] | 4 | [5 empty] | Wednesday | 600 | 1800 | 2400
Thursday | 600 | 1800 | 2500 | 5 | [5 empty] | 5 | [5 empty] | Thursday | 600 | 1800 | 2400
Friday | 600 | 1800 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 600 | 1800 | 2400 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 2600 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 600 | 2400 | 2400 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 600 | 2400 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 600 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 600 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 600 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 600 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 600 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 600 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 600 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 600 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 600 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 600 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | [5 empty] | 18 | [6 empty] | 600 | 2400 |  | 18 | [5 empty] | 18
|  |  |  | 19 | [5 empty] | 19 | [9 empty] | 19 | [5 empty] | 19
|  |  |  | 20 | [5 empty] | 20 | [9 empty] | 20 | [5 empty] | 20
|  |  |  | 21 | [5 empty] | 21 | [9 empty] | 21 | [5 empty] | 21
|  |  |  | 22 | [5 empty] | 22 | [9 empty] | 22 | [5 empty] | 22
|  |  |  | 23 | [5 empty] | 23 | [9 empty] | 23 | [5 empty] | 23
|  |  |  | 24 | [5 empty] | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 27 | [5 empty] | 8 | 19 | [6 empty] | 97.5 | 95 to 100 | 27 | [5 empty] | 8 | 19
92.5 | 90 to 95 | 68 | [5 empty] | 31 | 35 | 2 | [5 empty] | 92.5 | 90 to 95 | 68 | [5 empty] | 31 | 35 | 2
87.5 | 85 to 90 | 175 |  |  |  |  | 6 | 67 | 58 | 32 | 12 |  |  |  |  | 87.5 | 85 to 90 | 175 |  |  |  |  | 6 | 67 | 58 | 32 | 12
82.5 | 80 to 85 | 373 |  |  |  |  | 45 | 87 | 98 | 81 | 38 | 24 |  |  |  | 82.5 | 80 to 85 | 373 |  |  |  |  | 45 | 87 | 98 | 81 | 38 | 24
77.5 | 75 to 80 | 513 |  |  |  | 8 | 60 | 83 | 102 | 107 | 86 | 56 |  | 11 |  | 77.5 | 75 to 80 | 493 |  |  |  | 8 | 60 | 79 | 89 | 104 | 86 | 56 |  | 11
72.5 | 70 to 75 | 502 |  | 4 |  | 13 | 53 | 75 | 97 | 133 | 81 | 36 |  | 10 |  | 72.5 | 70 to 75 | 445 |  | 4 |  | 13 | 50 | 62 | 76 | 117 | 77 | 36 |  | 10
67.5 | 65 to 70 | 498 | 16 | 10 | 5 | 38 | 73 | 48 | 69 | 65 | 113 | 36 | 7 | 18 |  | 67.5 | 65 to 70 | 433 | 13 | 10 | 5 | 38 | 70 | 43 | 50 | 50 | 93 | 36 | 7 | 18
62.5 | 60 to 65 | 473 | 14 | 25 | 11 | 77 | 84 | 28 | 11 | 28 | 74 | 62 | 32 | 27 |  | 62.5 | 60 to 65 | 418 | 13 | 25 | 11 | 77 | 70 | 20 | 4 | 20 | 59 | 60 | 32 | 27
57.5 | 55 to 60 | 467 | 13 | 37 | 23 | 96 | 68 | 10 |  | 13 | 46 | 90 | 52 | 19 |  | 57.5 | 55 to 60 | 421 | 12 | 33 | 23 | 96 | 61 | 6 |  | 10 | 32 | 78 | 52 | 18
52.5 | 50 to 55 | 496 | 15 | 63 | 51 | 70 | 45 | 16 |  | 7 | 13 | 72 | 95 | 49 |  | 52.5 | 50 to 55 | 431 | 14 | 54 | 51 | 66 | 38 | 5 |  | 4 | 13 | 58 | 79 | 49
47.5 | 45 to 50 | 333 | 33 | 39 | 61 | 61 | 15 | 2 |  |  | 4 | 35 | 41 | 42 |  | 47.5 | 45 to 50 | 283 | 31 | 35 | 60 | 42 | 12 |  |  |  | 3 | 30 | 34 | 36
42.5 | 40 to 45 | 534 | 80 | 34 | 136 | 72 | 15 | 1 |  |  | 1 | 29 | 70 | 96 |  | 42.5 | 40 to 45 | 466 | 72 | 34 | 124 | 51 | 8 |  |  |  | 1 | 25 | 66 | 85
37.5 | 35 to 40 | 389 | 64 | 36 | 76 | 34 | 4 |  |  |  |  | 24 | 79 | 72 |  | 37.5 | 35 to 40 | 322 | 56 | 33 | 64 | 20 | [5 empty] | 14 | 73 | 62
32.5 | 30 to 35 | 291 | 57 | 46 | 73 | 10 | [5 empty] | 12 | 48 | 45 |  | 32.5 | 30 to 35 | 238 | 54 | 42 | 57 | 8 | [5 empty] | 6 | 39 | 32
27.5 | 25 to 30 | 157 | 35 | 51 | 19 | 1 | [5 empty] | 4 | 21 | 26 |  | 27.5 | 25 to 30 | 131 | 28 | 43 | 16 | 1 | [5 empty] | 3 | 15 | 25
22.5 | 20 to 25 | 170 | 69 | 26 | 9 | [7 empty] | 9 | 57 |  | 22.5 | 20 to 25 | 147 | 66 | 22 | 7 | [7 empty] | 9 | 43
17.5 | 15 to 20 | 104 | 49 | 31 | 4 | [7 empty] | 2 | 18 |  | 17.5 | 15 to 20 | 92 | 47 | 27 | 2 | [7 empty] | 2 | 14
12.5 | 10 to 15 | 57 | 34 | 21 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 39 | 19 | 18 | [9 empty] | 2
7.5 | 5 to 10 | 7 | 1 | 6 | [11 empty] | 7.5 | 5 to 10 | 2 | 1 | 1
2.5 | 0 to 5 | 2 |  | 2 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 5640 | [15 empty] | 5009
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | [5 empty] | 1 | [5 empty] | Sunday | 600 | 2400 | 2400
Monday | 600 | 1800 | 2500 | 2 | [5 empty] | 2 | [5 empty] | Monday | 600 | 1800 | 2400
Tuesday | 600 | 1800 | 2500 | 3 | [5 empty] | 3 | [5 empty] | Tuesday | 600 | 1800 | 2400
Wednesday | 600 | 1800 | 2500 | 4 | [5 empty] | 4 | [5 empty] | Wednesday | 600 | 1800 | 2400
Thursday | 600 | 1800 | 2500 | 5 | [5 empty] | 5 | [5 empty] | Thursday | 600 | 1800 | 2400
Friday | 600 | 1800 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 600 | 1800 | 2400 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 2600 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 600 | 2400 | 2600 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 600 | 2400 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 600 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 600 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 600 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 600 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 600 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 600 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 600 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 600 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 600 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 600 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | [5 empty] | 18 | [6 empty] | 600 | 2400 |  | 18 | [5 empty] | 18
|  |  |  | 19 | [5 empty] | 19 | [9 empty] | 19 | [5 empty] | 19
|  |  |  | 20 | [5 empty] | 20 | [9 empty] | 20 | [5 empty] | 20
|  |  |  | 21 | [5 empty] | 21 | [9 empty] | 21 | [5 empty] | 21
|  |  |  | 22 | [5 empty] | 22 | [9 empty] | 22 | [5 empty] | 22
|  |  |  | 23 | [5 empty] | 23 | [9 empty] | 23 | [5 empty] | 23
|  |  |  | 24 | [5 empty] | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 27 | [5 empty] | 8 | 19 | [6 empty] | 97.5 | 95 to 100 | 27 | [5 empty] | 8 | 19
92.5 | 90 to 95 | 68 | [5 empty] | 31 | 35 | 2 | [5 empty] | 92.5 | 90 to 95 | 68 | [5 empty] | 31 | 35 | 2
87.5 | 85 to 90 | 175 |  |  |  |  | 6 | 67 | 58 | 32 | 12 |  |  |  |  | 87.5 | 85 to 90 | 175 |  |  |  |  | 6 | 67 | 58 | 32 | 12
82.5 | 80 to 85 | 373 |  |  |  |  | 45 | 87 | 98 | 81 | 38 | 24 |  |  |  | 82.5 | 80 to 85 | 373 |  |  |  |  | 45 | 87 | 98 | 81 | 38 | 24
77.5 | 75 to 80 | 513 |  |  |  | 8 | 60 | 83 | 102 | 107 | 86 | 56 |  | 11 |  | 77.5 | 75 to 80 | 493 |  |  |  | 8 | 60 | 79 | 89 | 104 | 86 | 56 |  | 11
72.5 | 70 to 75 | 502 |  | 4 |  | 13 | 53 | 75 | 97 | 133 | 81 | 36 |  | 10 |  | 72.5 | 70 to 75 | 445 |  | 4 |  | 13 | 50 | 62 | 76 | 117 | 77 | 36 |  | 10
67.5 | 65 to 70 | 498 | 16 | 10 | 5 | 38 | 73 | 48 | 69 | 65 | 113 | 36 | 7 | 18 |  | 67.5 | 65 to 70 | 433 | 13 | 10 | 5 | 38 | 70 | 43 | 50 | 50 | 93 | 36 | 7 | 18
62.5 | 60 to 65 | 473 | 14 | 25 | 11 | 77 | 84 | 28 | 11 | 28 | 74 | 62 | 32 | 27 |  | 62.5 | 60 to 65 | 418 | 13 | 25 | 11 | 77 | 70 | 20 | 4 | 20 | 59 | 60 | 32 | 27
57.5 | 55 to 60 | 467 | 13 | 37 | 23 | 96 | 68 | 10 |  | 13 | 46 | 90 | 52 | 19 |  | 57.5 | 55 to 60 | 421 | 12 | 33 | 23 | 96 | 61 | 6 |  | 10 | 32 | 78 | 52 | 18
52.5 | 50 to 55 | 496 | 15 | 63 | 51 | 70 | 45 | 16 |  | 7 | 13 | 72 | 95 | 49 |  | 52.5 | 50 to 55 | 431 | 14 | 54 | 51 | 66 | 38 | 5 |  | 4 | 13 | 58 | 79 | 49
47.5 | 45 to 50 | 333 | 33 | 39 | 61 | 61 | 15 | 2 |  |  | 4 | 35 | 41 | 42 |  | 47.5 | 45 to 50 | 283 | 31 | 35 | 60 | 42 | 12 |  |  |  | 3 | 30 | 34 | 36
42.5 | 40 to 45 | 534 | 80 | 34 | 136 | 72 | 15 | 1 |  |  | 1 | 29 | 70 | 96 |  | 42.5 | 40 to 45 | 466 | 72 | 34 | 124 | 51 | 8 |  |  |  | 1 | 25 | 66 | 85
37.5 | 35 to 40 | 389 | 64 | 36 | 76 | 34 | 4 |  |  |  |  | 24 | 79 | 72 |  | 37.5 | 35 to 40 | 322 | 56 | 33 | 64 | 20 | [5 empty] | 14 | 73 | 62
32.5 | 30 to 35 | 291 | 57 | 46 | 73 | 10 | [5 empty] | 12 | 48 | 45 |  | 32.5 | 30 to 35 | 238 | 54 | 42 | 57 | 8 | [5 empty] | 6 | 39 | 32
27.5 | 25 to 30 | 157 | 35 | 51 | 19 | 1 | [5 empty] | 4 | 21 | 26 |  | 27.5 | 25 to 30 | 131 | 28 | 43 | 16 | 1 | [5 empty] | 3 | 15 | 25
22.5 | 20 to 25 | 170 | 69 | 26 | 9 | [7 empty] | 9 | 57 |  | 22.5 | 20 to 25 | 147 | 66 | 22 | 7 | [7 empty] | 9 | 43
17.5 | 15 to 20 | 104 | 49 | 31 | 4 | [7 empty] | 2 | 18 |  | 17.5 | 15 to 20 | 92 | 47 | 27 | 2 | [7 empty] | 2 | 14
12.5 | 10 to 15 | 57 | 34 | 21 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 39 | 19 | 18 | [9 empty] | 2
7.5 | 5 to 10 | 7 | 1 | 6 | [11 empty] | 7.5 | 5 to 10 | 2 | 1 | 1
2.5 | 0 to 5 | 2 |  | 2 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 5640 | [15 empty] | 5009
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 600 | 2300 | 2300 | [12 empty] | Sunday | 600 | 2200 | 2200
Monday | 600 | 2300 | 2300 | [12 empty] | Monday | 600 | 2200 | 2200
Tuesday | 600 | 2300 | 2300 | [12 empty] | Tuesday | 600 | 2200 | 2200
Wednesday | 600 | 2300 | 2300 | [12 empty] | Wednesday | 600 | 2200 | 2200
Thursday | 600 | 2300 | 2300 | [12 empty] | Thursday | 600 | 2200 | 2200
Friday | 600 | 2300 | 2300 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 600 | 2200 | 2200 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 600 | 2300 | 2700 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 600 | 2200 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 600 | 2300 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 600 | 2200 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 600 | 2300 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 600 | 2200 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 600 | 2300 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 600 | 2200 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 600 | 2300 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 600 | 2200 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 600 | 2300 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 600 | 2200 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 600 | 2300 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 600 | 2200 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 600 | 2300 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 600 | 2200 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12
82.5 | 80 to 85 | 417 |  |  |  |  | 51 | 97 | 118 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24
77.5 | 75 to 80 | 577 |  |  |  | 9 | 67 | 103 | 114 | 124 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 561 |  |  |  | 9 | 65 | 99 | 107 | 121 | 93 | 56 |  | 11
72.5 | 70 to 75 | 577 |  | 4 |  | 13 | 65 | 101 | 99 | 156 | 91 | 38 |  | 10 |  | 72.5 | 70 to 75 | 538 |  | 4 |  | 13 | 65 | 89 | 88 | 143 | 88 | 38 |  | 10
67.5 | 65 to 70 | 582 | 15 | 10 | 6 | 42 | 95 | 62 | 61 | 76 | 123 | 61 | 7 | 24 |  | 67.5 | 65 to 70 | 541 | 15 | 10 | 6 | 42 | 89 | 54 | 53 | 70 | 115 | 57 | 7 | 23
62.5 | 60 to 65 | 537 | 20 | 26 | 14 | 89 | 92 | 21 | 6 | 34 | 84 | 79 | 34 | 38 |  | 62.5 | 60 to 65 | 492 | 19 | 24 | 14 | 88 | 80 | 18 | 4 | 27 | 75 | 75 | 33 | 35
57.5 | 55 to 60 | 521 | 13 | 48 | 29 | 123 | 73 | 9 |  | 11 | 44 | 88 | 61 | 22 |  | 57.5 | 55 to 60 | 492 | 12 | 47 | 28 | 117 | 72 | 7 |  | 9 | 38 | 83 | 59 | 20
52.5 | 50 to 55 | 556 | 18 | 71 | 67 | 80 | 52 | 5 |  | 4 | 19 | 81 | 94 | 65 |  | 52.5 | 50 to 55 | 526 | 17 | 65 | 66 | 74 | 48 | 4 |  | 4 | 16 | 75 | 93 | 64
47.5 | 45 to 50 | 374 | 40 | 41 | 73 | 67 | 19 |  |  |  | 3 | 39 | 51 | 41 |  | 47.5 | 45 to 50 | 348 | 40 | 41 | 67 | 61 | 14 |  |  |  | 2 | 37 | 47 | 39
42.5 | 40 to 45 | 562 | 87 | 46 | 151 | 56 | 6 |  |  |  | 1 | 40 | 80 | 95 |  | 42.5 | 40 to 45 | 515 | 81 | 41 | 142 | 47 | 5 |  |  |  | 1 | 34 | 74 | 90
37.5 | 35 to 40 | 391 | 67 | 39 | 79 | 22 | [5 empty] | 14 | 96 | 74 |  | 37.5 | 35 to 40 | 361 | 62 | 37 | 73 | 22 | [5 empty] | 12 | 87 | 68
32.5 | 30 to 35 | 303 | 72 | 47 | 73 | 8 | [5 empty] | 5 | 47 | 51 |  | 32.5 | 30 to 35 | 285 | 68 | 46 | 70 | 6 | [5 empty] | 3 | 44 | 48
27.5 | 25 to 30 | 178 | 30 | 61 | 24 | 1 | [5 empty] | 2 | 23 | 37 |  | 27.5 | 25 to 30 | 163 | 28 | 56 | 21 | 1 | [5 empty] | 2 | 22 | 33
22.5 | 20 to 25 | 174 | 80 | 29 | 9 | [7 empty] | 14 | 42 |  | 22.5 | 20 to 25 | 161 | 75 | 27 | 7 | [7 empty] | 12 | 40
17.5 | 15 to 20 | 120 | 65 | 34 | 2 | [7 empty] | 3 | 16 |  | 17.5 | 15 to 20 | 112 | 61 | 32 | 2 | [7 empty] | 2 | 15
12.5 | 10 to 15 | 36 | 19 | 16 | [9 empty] | 1 |  | 12.5 | 10 to 15 | 31 | 17 | 14
7.5 | 5 to 10 | 2 | 1 | 1 | [11 empty] | 7.5 | 5 to 10 | 2 | 1 | 1
2.5 | 0 to 5 | 2 |  | 2 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 6204 | [15 empty] | 5839
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 |  |  |  |  | 1 | 1 | [5 empty] | Sunday | 500 | 2400 | 2400
Monday | 0 | 100 | 2500 | 2 |  |  |  |  | 2 | 2 | [5 empty] | Monday | 0 | 100 | 2400
Tuesday | 0 | 100 | 2500 | 3 |  |  |  |  | 3 | 3 | [5 empty] | Tuesday | 0 | 100 | 2400
Wednesday | 0 | 100 | 2500 | 4 |  |  |  |  | 4 | 4 | [5 empty] | Wednesday | 0 | 100 | 2400
Thursday | 0 | 100 | 2500 | 5 |  |  |  |  | 5 | 5 | [5 empty] | Thursday | 0 | 100 | 2400 | 5 |  |  |  |  | 5 | 5
Friday | 0 | 2400 | 2500 | 6 |  |  |  |  | 6 | 6 | [5 empty] | Friday | 500 | 2400 | 2400 | 6 |  |  |  |  | 6 | 6
Saturday | 0 | 2400 | 2500 | 7 |  |  |  |  | 7 | 7 | [5 empty] | Saturday | 500 | 2400 | 2400 | 7 |  |  |  |  | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 |  |  |  |  | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 |  |  |  |  | 8 | 8
|  |  |  | 9 |  |  |  |  | 9 | 9 | [9 empty] | 9 |  |  |  |  | 9 | 9
|  |  |  | 10 |  |  |  |  | 10 | 10 | [9 empty] | 10 |  |  |  |  | 10 | 10
|  |  |  | 11 |  |  |  |  | 11 | 11 | [9 empty] | 11 |  |  |  |  | 11 | 11
| 100 | 2500 |  | 12 |  |  |  |  | 12 | 12 | [6 empty] | 500 | 2400 |  | 12 |  |  |  |  | 12 | 12
| 0 | 100 |  | 13 |  |  |  |  | 13 | 13 | [6 empty] | 0 | 100 |  | 13 |  |  |  |  | 13 | 13
| 0 | 100 |  | 14 |  |  |  |  | 14 | 14 | [6 empty] | 0 | 100 |  | 14 |  |  |  |  | 14 | 14
| 0 | 100 |  | 15 |  |  |  |  | 15 | 15 | [6 empty] | 0 | 100 |  | 15 |  |  |  |  | 15 | 15
| 0 | 100 |  | 16 |  |  |  |  | 16 | 16 | [6 empty] | 0 | 100 |  | 16 |  |  |  |  | 16 | 16
| 100 | 2500 |  | 17 |  |  |  |  | 17 | 17 | [6 empty] | 500 | 2400 |  | 17 |  |  |  |  | 17 | 17
| 100 | 2500 |  | 18 |  |  |  |  | 18 | 18 | [6 empty] | 500 | 2400 |  | 18 |  |  |  |  | 18 | 18
|  |  |  | 19 |  |  |  |  | 19 | 19 | [9 empty] | 19 |  |  |  |  | 19 | 19
|  |  |  | 20 |  |  |  |  | 20 | 20 | [9 empty] | 20 |  |  |  |  | 20 | 20
|  |  |  | 21 |  |  |  |  | 21 | 21 | [9 empty] | 21 |  |  |  |  | 21 | 21
|  |  |  | 22 |  |  |  |  | 22 | 22 | [9 empty] | 22 |  |  |  |  | 22 | 22
|  |  |  | 23 |  |  |  |  | 23 | 23 | [9 empty] | 23 |  |  |  |  | 23 | 23
|  |  |  | 24 |  |  |  |  | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 16 | [5 empty] | 1 | 15 | [6 empty] | 97.5 | 95 to 100 | 16 | [5 empty] | 1 | 15
92.5 | 90 to 95 | 19 | [5 empty] | 5 | 13 | 1 | [5 empty] | 92.5 | 90 to 95 | 19 | [5 empty] | 5 | 13 | 1
87.5 | 85 to 90 | 86 |  |  |  |  | 1 | 23 | 32 | 23 | 7 |  |  |  |  | 87.5 | 85 to 90 | 86 |  |  |  |  | 1 | 23 | 32 | 23 | 7
82.5 | 80 to 85 | 184 |  |  |  |  | 21 | 41 | 58 | 41 | 21 | 2 |  |  |  | 82.5 | 80 to 85 | 183 |  |  |  |  | 21 | 41 | 57 | 41 | 21 | 2
77.5 | 75 to 80 | 256 |  |  |  | 3 | 25 | 43 | 71 | 49 | 44 | 21 |  |  |  | 77.5 | 75 to 80 | 231 |  |  |  | 3 | 25 | 38 | 55 | 45 | 44 | 21
72.5 | 70 to 75 | 350 |  | 4 |  | 8 | 29 | 70 | 76 | 89 | 62 | 12 |  |  |  | 72.5 | 70 to 75 | 276 |  | 4 |  | 8 | 26 | 53 | 49 | 69 | 55 | 12
67.5 | 65 to 70 | 375 | 14 | 5 |  | 21 | 39 | 57 | 52 | 52 | 91 | 25 | 10 | 9 |  | 67.5 | 65 to 70 | 287 | 11 | 5 |  | 21 | 35 | 45 | 35 | 31 | 67 | 21 | 7 | 9
62.5 | 60 to 65 | 292 | 10 | 10 |  | 36 | 49 | 30 | 16 | 14 | 62 | 34 | 10 | 21 |  | 62.5 | 60 to 65 | 219 | 8 | 10 |  | 32 | 33 | 20 | 7 | 8 | 40 | 32 | 10 | 19
57.5 | 55 to 60 | 322 | 8 | 21 | 10 | 63 | 49 | 16 |  | 15 | 36 | 58 | 27 | 19 |  | 57.5 | 55 to 60 | 258 | 8 | 17 | 10 | 61 | 39 | 11 |  | 8 | 24 | 42 | 27 | 11
52.5 | 50 to 55 | 354 | 6 | 45 | 27 | 47 | 32 | 23 |  | 4 | 3 | 60 | 69 | 38 |  | 52.5 | 50 to 55 | 278 | 5 | 31 | 27 | 39 | 25 | 9 |  | 2 | 3 | 47 | 55 | 35
47.5 | 45 to 50 | 239 | 12 | 26 | 34 | 54 | 21 | 2 |  |  | 4 | 31 | 25 | 30 |  | 47.5 | 45 to 50 | 183 | 10 | 24 | 32 | 36 | 14 |  |  |  | 3 | 23 | 17 | 24
42.5 | 40 to 45 | 382 | 63 | 18 | 91 | 61 | 18 | 1 |  |  | 6 | 33 | 40 | 51 |  | 42.5 | 40 to 45 | 290 | 52 | 14 | 76 | 40 | 8 | 1 |  |  | 2 | 25 | 30 | 42
37.5 | 35 to 40 | 300 | 36 | 14 | 65 | 35 | 4 |  |  |  |  | 22 | 58 | 66 |  | 37.5 | 35 to 40 | 218 | 25 | 11 | 46 | 20 | 1 |  |  |  |  | 14 | 50 | 51
32.5 | 30 to 35 | 179 | 28 | 28 | 50 | 8 | [5 empty] | 10 | 25 | 30 |  | 32.5 | 30 to 35 | 132 | 25 | 25 | 35 | 6 | [5 empty] | 4 | 18 | 19
27.5 | 25 to 30 | 118 | 35 | 28 | 17 | [6 empty] | 4 | 11 | 23 |  | 27.5 | 25 to 30 | 84 | 22 | 19 | 12 | [6 empty] | 4 | 5 | 22
22.5 | 20 to 25 | 152 | 41 | 27 | 16 | [7 empty] | 8 | 60 |  | 22.5 | 20 to 25 | 115 | 37 | 20 | 8 | [7 empty] | 7 | 43
17.5 | 15 to 20 | 87 | 34 | 35 | 2 | [7 empty] | 5 | 11 |  | 17.5 | 15 to 20 | 70 | 32 | 27 | 1 | [7 empty] | 2 | 8
12.5 | 10 to 15 | 46 | 25 | 19 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 31 | 12 | 17 | [9 empty] | 2
7.5 | 5 to 10 | 5 |  | 5 | [11 empty] | 7.5 | 5 to 10 | 1 |  | 1
2.5 | 0 to 5 | 2 |  | 2 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 3768 | [15 empty] | 2982
#REF!
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
#REF!
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 700 | 1400 | 1400 |  | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 1400 |  | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 1400 |  | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500
Wednesday | 0 | 2400 | 1400 |  | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500
Thursday | 0 | 2400 | 1400 |  | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 |  | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 5000 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 700 | 1400 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  |  | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  |  | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  |  | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  |  | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
[5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
[5 empty] | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
[5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
[5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
[5 empty] | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[5 empty] | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 31 | [5 empty] | 11 | 20 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12 |  |  |  |  | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24 |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
77.5 | 75 to 80 | 570 |  |  |  | 9 | 65 | 99 | 114 | 123 | 93 | 56 |  | 11 |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
72.5 | 70 to 75 | 602 |  | 4 |  | 13 | 66 | 110 | 112 | 159 | 88 | 40 |  | 10 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
67.5 | 65 to 70 | 628 | 16 | 10 | 6 | 42 | 91 | 75 | 75 | 88 | 134 | 59 | 7 | 25 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
62.5 | 60 to 65 | 556 | 21 | 24 | 14 | 91 | 97 | 28 | 13 | 37 | 83 | 77 | 33 | 38 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
57.5 | 55 to 60 | 562 | 13 | 49 | 30 | 122 | 85 | 7 |  | 18 | 56 | 94 | 61 | 27 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
[16 empty] | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
[16 empty] | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
[16 empty] | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
52.5 | 50 to 55 | 604 | 17 | 76 | 67 | 82 | 55 | 10 |  | 11 | 28 | 90 | 102 | 66 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
47.5 | 45 to 50 | 389 | 44 | 46 | 68 | 67 | 24 | 1 |  |  | 3 | 41 | 52 | 43 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
42.5 | 40 to 45 | 604 | 92 | 47 | 161 | 63 | 13 | 1 |  |  | 3 | 48 | 78 | 98 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
37.5 | 35 to 40 | 443 | 68 | 43 | 84 | 41 | 4 |  |  |  |  | 20 | 103 | 80 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
32.5 | 30 to 35 | 338 | 76 | 50 | 88 | 7 | [5 empty] | 6 | 53 | 58 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
27.5 | 25 to 30 | 188 | 35 | 59 | 23 | 3 | [5 empty] | 3 | 31 | 34 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
22.5 | 20 to 25 | 191 | 83 | 32 | 11 | [7 empty] | 18 | 47 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
17.5 | 15 to 20 | 136 | 66 | 41 | 6 | [7 empty] | 2 | 21 |  | 7.5 | 5 to 10 | 5 | 1 | 4
12.5 | 10 to 15 | 41 | 26 | 15 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
7.5 | 5 to 10 | 9 | 3 | 6 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 6570 | [15 empty] | 7664
#REF!
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 500 | 2200 | 2200 | [12 empty] | Sunday | 500 | 2100 | 2100
Monday | 500 | 2200 | 2200 | [12 empty] | Monday | 500 | 2100 | 2100
Tuesday | 500 | 2200 | 2200 | [12 empty] | Tuesday | 500 | 2100 | 2100
Wednesday | 500 | 2200 | 2200 | [12 empty] | Wednesday | 500 | 2100 | 2100
Thursday | 500 | 2200 | 2200 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 500 | 2100 | 2100 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 500 | 2200 | 2200 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 500 | 2100 | 2100 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 500 | 2200 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 500 | 2100 | 2400 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 500 | 2200 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 500 | 2100 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 500 | 2200 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 500 | 2100 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 500 | 2200 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 500 | 2100 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 500 | 2200 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 500 | 2100 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 500 | 2200 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 500 | 2100 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 500 | 2200 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 500 | 2100 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 500 | 2200 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 500 | 2100 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 190 |  |  |  |  | 7 | 72 | 66 | 33 | 12
82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 409 |  |  |  |  | 50 | 97 | 113 | 85 | 40 | 24
77.5 | 75 to 80 | 564 |  |  |  | 9 | 65 | 99 | 109 | 122 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 547 |  |  |  | 9 | 65 | 93 | 100 | 120 | 93 | 56 |  | 11
72.5 | 70 to 75 | 571 |  | 4 |  | 13 | 65 | 101 | 100 | 151 | 88 | 39 |  | 10 |  | 72.5 | 70 to 75 | 529 |  | 4 |  | 13 | 64 | 88 | 89 | 139 | 83 | 39 |  | 10
67.5 | 65 to 70 | 582 | 15 | 10 | 6 | 42 | 90 | 63 | 64 | 79 | 124 | 58 | 7 | 24 |  | 67.5 | 65 to 70 | 536 | 15 | 10 | 6 | 42 | 81 | 57 | 58 | 70 | 114 | 52 | 7 | 24
62.5 | 60 to 65 | 526 | 20 | 24 | 14 | 90 | 88 | 23 | 10 | 32 | 79 | 76 | 33 | 37 |  | 62.5 | 60 to 65 | 485 | 18 | 23 | 14 | 89 | 80 | 19 | 9 | 28 | 71 | 69 | 32 | 33
57.5 | 55 to 60 | 525 | 13 | 48 | 29 | 119 | 79 | 7 |  | 13 | 47 | 87 | 60 | 23 |  | 57.5 | 55 to 60 | 499 | 13 | 46 | 28 | 111 | 75 | 6 |  | 11 | 44 | 86 | 58 | 21
52.5 | 50 to 55 | 567 | 17 | 70 | 67 | 78 | 51 | 7 |  | 8 | 23 | 84 | 97 | 65 |  | 52.5 | 50 to 55 | 533 | 17 | 64 | 61 | 73 | 48 | 7 |  | 8 | 20 | 78 | 93 | 64
47.5 | 45 to 50 | 367 | 42 | 44 | 67 | 64 | 20 |  |  |  | 2 | 38 | 50 | 40 |  | 47.5 | 45 to 50 | 338 | 40 | 44 | 65 | 54 | 15 |  |  |  | 1 | 35 | 47 | 37
42.5 | 40 to 45 | 562 | 86 | 44 | 152 | 55 | 9 | 1 |  |  | 2 | 42 | 76 | 95 |  | 42.5 | 40 to 45 | 520 | 79 | 38 | 142 | 51 | 9 | 1 |  |  | 2 | 37 | 70 | 91
37.5 | 35 to 40 | 404 | 66 | 40 | 78 | 32 | 2 |  |  |  |  | 16 | 95 | 75 |  | 37.5 | 35 to 40 | 378 | 62 | 39 | 73 | 31 | 2 |  |  |  |  | 14 | 87 | 70
32.5 | 30 to 35 | 307 | 71 | 48 | 78 | 6 | [5 empty] | 4 | 48 | 52 |  | 32.5 | 30 to 35 | 292 | 69 | 47 | 74 | 5 | [5 empty] | 3 | 46 | 48
27.5 | 25 to 30 | 177 | 32 | 57 | 23 | 2 | [5 empty] | 3 | 27 | 33 |  | 27.5 | 25 to 30 | 160 | 29 | 52 | 20 | 2 | [5 empty] | 3 | 25 | 29
22.5 | 20 to 25 | 176 | 78 | 30 | 9 | [7 empty] | 15 | 44 |  | 22.5 | 20 to 25 | 166 | 74 | 28 | 9 | [7 empty] | 13 | 42
17.5 | 15 to 20 | 125 | 65 | 36 | 4 | [7 empty] | 2 | 18 |  | 17.5 | 15 to 20 | 114 | 58 | 34 | 4 | [7 empty] | 2 | 16
12.5 | 10 to 15 | 36 | 21 | 15 | [11 empty] | 12.5 | 10 to 15 | 34 | 21 | 13
7.5 | 5 to 10 | 4 | 1 | 3 | [11 empty] | 7.5 | 5 to 10 | 4 | 1 | 3
2.5 | 0 to 5 | 2 |  | 2 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 6205 | [15 empty] | 5839
#REF!
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [11 empty] | PROPOSED HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | 100 | 2400 | 2500
Tuesday | 0 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | 100 | 2400 | 2500
Wednesday | 0 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | 100 | 2400 | 2500
Thursday | 0 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 0 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [6 empty] | 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [6 empty] | 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [6 empty] | 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [9 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [9 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | [6 empty] | 102.5 | 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 624 |  |  |  | 9 | 68 | 112 | 140 | 135 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 716 |  | 4 |  | 13 | 67 | 145 | 144 | 195 | 97 | 41 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 747 | 15 | 10 | 6 | 42 | 112 | 94 | 98 | 108 | 155 | 71 | 8 | 28
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 688 | 27 | 29 | 14 | 94 | 126 | 38 | 19 | 54 | 116 | 91 | 36 | 44
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 657 | 14 | 54 | 33 | 133 | 95 | 17 |  | 28 | 74 | 110 | 63 | 36
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 686 | 19 | 93 | 68 | 110 | 66 | 14 |  | 9 | 32 | 102 | 105 | 68
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 483 | 48 | 46 | 85 | 90 | 38 |  |  |  | 7 | 49 | 69 | 51
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 726 | 104 | 56 | 184 | 84 | 18 | 1 |  |  | 4 | 68 | 97 | 110
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 540 | 85 | 54 | 110 | 39 | 3 |  |  |  |  | 24 | 123 | 102
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 395 | 86 | 57 | 95 | 14 | [5 empty] | 11 | 67 | 65
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 239 | 48 | 73 | 35 | 2 | [5 empty] | 4 | 34 | 43
22.5 | 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70 |  | 22.5 | 20 to 25 | 231 | 94 | 39 | 17 | [7 empty] | 23 | 58
17.5 | 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29 |  | 17.5 | 15 to 20 | 153 | 77 | 44 | 4 | [7 empty] | 5 | 23
12.5 | 10 to 15 | 71 | 47 | 22 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 57 | 33 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [11 empty] | 7.5 | 5 to 10 | 5 | 1 | 4
2.5 | 0 to 5 | 4 |  | 4 | [11 empty] | 2.5 | 0 to 5 | 2 |  | 2
-2.5 | -5 to 0 | 1 |  | 1 | [11 empty] | -2.5 | -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 7664
0
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! | [13 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! | [13 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! | [13 empty] | Tuesday | #REF! | #REF!
Wednesday | #REF! | #REF! | [13 empty] | Wednesday | #REF! | #REF!
Thursday | #REF! | #REF! | [13 empty] | Thursday | #REF! | #REF!
Friday | #REF! | #REF! | [13 empty] | Friday | #REF! | #REF!
Saturday | #REF! | #REF! | [13 empty] | Saturday | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 31 | [5 empty] | 11 | 20 | [6 empty] | 97.5 | 95 to 100 | 31 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 71 | [5 empty] | 32 | 37 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 189 |  |  |  |  | 7 | 72 | 65 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12
82.5 | 80 to 85 | 411 |  |  |  |  | 51 | 97 | 115 | 84 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24
77.5 | 75 to 80 | 579 |  |  |  | 9 | 67 | 104 | 117 | 123 | 92 | 56 |  | 11 |  | 77.5 | 75 to 80 | 553 |  |  |  | 9 | 65 | 98 | 101 | 120 | 93 | 56 |  | 11
72.5 | 70 to 75 | 614 |  | 4 |  | 13 | 64 | 117 | 119 | 162 | 85 | 40 |  | 10 |  | 72.5 | 70 to 75 | 504 |  | 4 |  | 13 | 64 | 76 | 79 | 135 | 86 | 37 |  | 10
67.5 | 65 to 70 | 642 | 15 | 10 | 6 | 42 | 87 | 76 | 77 | 95 | 138 | 58 | 8 | 30 |  | 67.5 | 65 to 70 | 500 | 15 | 10 | 6 | 42 | 87 | 47 | 39 | 61 | 108 | 56 | 7 | 22
62.5 | 60 to 65 | 577 | 18 | 24 | 14 | 92 | 106 | 30 | 16 | 42 | 84 | 76 | 35 | 40 |  | 62.5 | 60 to 65 | 464 | 19 | 24 | 14 | 87 | 71 | 14 | 2 | 21 | 71 | 74 | 33 | 34
57.5 | 55 to 60 | 578 | 13 | 45 | 29 | 122 | 84 | 6 |  | 22 | 64 | 99 | 64 | 30 |  | 57.5 | 55 to 60 | 462 | 10 | 46 | 28 | 114 | 68 | 6 |  | 6 | 30 | 78 | 59 | 17
52.5 | 50 to 55 | 607 | 18 | 80 | 63 | 86 | 55 | 11 |  | 13 | 28 | 93 | 98 | 62 |  | 52.5 | 50 to 55 | 477 | 17 | 60 | 64 | 71 | 40 |  |  |  | 8 | 67 | 88 | 62
47.5 | 45 to 50 | 411 | 48 | 45 | 74 | 72 | 28 | 1 |  |  | 3 | 42 | 53 | 45 |  | 47.5 | 45 to 50 | 332 | 39 | 38 | 67 | 55 | 12 |  |  |  | 2 | 35 | 45 | 39
42.5 | 40 to 45 | 621 | 94 | 53 | 161 | 64 | 17 | 1 |  |  | 4 | 47 | 81 | 99 |  | 42.5 | 40 to 45 | 472 | 77 | 39 | 132 | 41 | [5 empty] | 27 | 72 | 84
37.5 | 35 to 40 | 461 | 72 | 42 | 88 | 42 | 4 |  |  |  |  | 24 | 107 | 82 |  | 37.5 | 35 to 40 | 319 | 56 | 33 | 68 | 13 | [5 empty] | 8 | 79 | 62
32.5 | 30 to 35 | 350 | 78 | 55 | 89 | 7 | [5 empty] | 6 | 57 | 58 |  | 32.5 | 30 to 35 | 259 | 65 | 44 | 62 | 5 | [5 empty] | 2 | 38 | 43
27.5 | 25 to 30 | 196 | 36 | 62 | 25 | 3 | [5 empty] | 3 | 34 | 33 |  | 27.5 | 25 to 30 | 149 | 24 | 53 | 19 | [6 empty] | 1 | 19 | 33
22.5 | 20 to 25 | 204 | 83 | 35 | 20 | [7 empty] | 18 | 48 |  | 22.5 | 20 to 25 | 147 | 73 | 26 | 4 | [7 empty] | 8 | 36
17.5 | 15 to 20 | 130 | 62 | 38 | 6 | [7 empty] | 4 | 20 |  | 17.5 | 15 to 20 | 100 | 57 | 28 | 1 | [7 empty] | 2 | 12
12.5 | 10 to 15 | 45 | 30 | 15 | [11 empty] | 12.5 | 10 to 15 | 24 | 12 | 12
7.5 | 5 to 10 | 9 | 3 | 6 | [11 empty] | 7.5 | 5 to 10 | 4 | 2 | 2
|  | 6726 | [15 empty] | 5475
0
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | Tuesday | #REF! | #REF!
Wednesday | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | Wednesday | #REF! | #REF!
Thursday | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | Thursday | #REF! | #REF!
Friday | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | Friday | #REF! | #REF!
Saturday | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | Saturday | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 31 | [5 empty] | 11 | 20 | [6 empty] | 97.5 | 95 to 100 | 31 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 71 | [5 empty] | 32 | 37 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 189 |  |  |  |  | 7 | 72 | 65 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12
82.5 | 80 to 85 | 411 |  |  |  |  | 51 | 97 | 115 | 84 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24
77.5 | 75 to 80 | 579 |  |  |  | 9 | 67 | 104 | 117 | 123 | 92 | 56 |  | 11 |  | 77.5 | 75 to 80 | 553 |  |  |  | 9 | 65 | 98 | 101 | 120 | 93 | 56 |  | 11
72.5 | 70 to 75 | 614 |  | 4 |  | 13 | 64 | 117 | 119 | 162 | 85 | 40 |  | 10 |  | 72.5 | 70 to 75 | 504 |  | 4 |  | 13 | 64 | 76 | 79 | 135 | 86 | 37 |  | 10
67.5 | 65 to 70 | 642 | 15 | 10 | 6 | 42 | 87 | 76 | 77 | 95 | 138 | 58 | 8 | 30 |  | 67.5 | 65 to 70 | 500 | 15 | 10 | 6 | 42 | 87 | 47 | 39 | 61 | 108 | 56 | 7 | 22
62.5 | 60 to 65 | 577 | 18 | 24 | 14 | 92 | 106 | 30 | 16 | 42 | 84 | 76 | 35 | 40 |  | 62.5 | 60 to 65 | 464 | 19 | 24 | 14 | 87 | 71 | 14 | 2 | 21 | 71 | 74 | 33 | 34
57.5 | 55 to 60 | 578 | 13 | 45 | 29 | 122 | 84 | 6 |  | 22 | 64 | 99 | 64 | 30 |  | 57.5 | 55 to 60 | 462 | 10 | 46 | 28 | 114 | 68 | 6 |  | 6 | 30 | 78 | 59 | 17
52.5 | 50 to 55 | 607 | 18 | 80 | 63 | 86 | 55 | 11 |  | 13 | 28 | 93 | 98 | 62 |  | 52.5 | 50 to 55 | 477 | 17 | 60 | 64 | 71 | 40 |  |  |  | 8 | 67 | 88 | 62
47.5 | 45 to 50 | 411 | 48 | 45 | 74 | 72 | 28 | 1 |  |  | 3 | 42 | 53 | 45 |  | 47.5 | 45 to 50 | 332 | 39 | 38 | 67 | 55 | 12 |  |  |  | 2 | 35 | 45 | 39
42.5 | 40 to 45 | 621 | 94 | 53 | 161 | 64 | 17 | 1 |  |  | 4 | 47 | 81 | 99 |  | 42.5 | 40 to 45 | 472 | 77 | 39 | 132 | 41 | [5 empty] | 27 | 72 | 84
37.5 | 35 to 40 | 461 | 72 | 42 | 88 | 42 | 4 |  |  |  |  | 24 | 107 | 82 |  | 37.5 | 35 to 40 | 319 | 56 | 33 | 68 | 13 | [5 empty] | 8 | 79 | 62
32.5 | 30 to 35 | 350 | 78 | 55 | 89 | 7 | [5 empty] | 6 | 57 | 58 |  | 32.5 | 30 to 35 | 259 | 65 | 44 | 62 | 5 | [5 empty] | 2 | 38 | 43
27.5 | 25 to 30 | 196 | 36 | 62 | 25 | 3 | [5 empty] | 3 | 34 | 33 |  | 27.5 | 25 to 30 | 149 | 24 | 53 | 19 | [6 empty] | 1 | 19 | 33
22.5 | 20 to 25 | 204 | 83 | 35 | 20 | [7 empty] | 18 | 48 |  | 22.5 | 20 to 25 | 147 | 73 | 26 | 4 | [7 empty] | 8 | 36
17.5 | 15 to 20 | 130 | 62 | 38 | 6 | [7 empty] | 4 | 20 |  | 17.5 | 15 to 20 | 100 | 57 | 28 | 1 | [7 empty] | 2 | 12
12.5 | 10 to 15 | 45 | 30 | 15 | [11 empty] | 12.5 | 10 to 15 | 24 | 12 | 12
7.5 | 5 to 10 | 9 | 3 | 6 | [11 empty] | 7.5 | 5 to 10 | 4 | 2 | 2
|  | 6726 | [15 empty] | 5475
0
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! | [13 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! | [13 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! | [13 empty] | Tuesday | #REF! | #REF!
Wednesday | #REF! | #REF! | [13 empty] | Wednesday | #REF! | #REF!
Thursday | #REF! | #REF! | [13 empty] | Thursday | #REF! | #REF!
Friday | #REF! | #REF! | [13 empty] | Friday | #REF! | #REF!
Saturday | #REF! | #REF! | [13 empty] | Saturday | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 4 | [5 empty] | 1 | 2 | 1 | [5 empty] | 97.5 | 95 to 100 | 4 | [5 empty] | 1 | 2 | 1
92.5 | 90 to 95 | 94 |  |  |  |  | 12 | 16 | 40 | 26 | [5 empty] | 92.5 | 90 to 95 | 94 |  |  |  |  | 12 | 16 | 40 | 26
87.5 | 85 to 90 | 239 |  |  |  |  | 30 | 40 | 88 | 71 | 10 |  |  |  |  | 87.5 | 85 to 90 | 239 |  |  |  |  | 30 | 40 | 88 | 71 | 10
82.5 | 80 to 85 | 492 |  |  | 5 |  | 42 | 114 | 133 | 138 | 57 | 3 |  |  |  | 82.5 | 80 to 85 | 492 |  |  | 5 |  | 42 | 114 | 133 | 138 | 57 | 3
77.5 | 75 to 80 | 695 |  |  | 7 | 4 | 61 | 143 | 190 | 147 | 119 | 24 |  |  |  | 77.5 | 75 to 80 | 695 |  |  | 7 | 4 | 61 | 143 | 190 | 147 | 119 | 24
72.5 | 70 to 75 | 753 |  |  | 14 | 23 | 65 | 135 | 186 | 163 | 139 | 26 |  | 2 |  | 72.5 | 70 to 75 | 753 |  |  | 14 | 23 | 65 | 135 | 186 | 163 | 139 | 26 |  | 2
67.5 | 65 to 70 | 762 |  | 4 | 17 | 74 | 121 | 134 | 85 | 128 | 136 | 50 | 7 | 6 |  | 67.5 | 65 to 70 | 762 |  | 4 | 17 | 74 | 121 | 134 | 85 | 128 | 136 | 50 | 7 | 6
62.5 | 60 to 65 | 903 |  | 27 | 48 | 120 | 167 | 96 | 20 | 62 | 148 | 106 | 79 | 30 |  | 62.5 | 60 to 65 | 903 |  | 27 | 48 | 120 | 167 | 96 | 20 | 62 | 148 | 106 | 79 | 30
57.5 | 55 to 60 | 721 | 17 | 10 | 59 | 148 | 109 | 25 |  | 8 | 82 | 156 | 89 | 18 |  | 57.5 | 55 to 60 | 721 | 17 | 10 | 59 | 148 | 109 | 25 |  | 8 | 82 | 156 | 89 | 18
52.5 | 50 to 55 | 813 | 11 | 32 | 109 | 203 | 89 | 15 |  |  | 28 | 149 | 132 | 45 |  | 52.5 | 50 to 55 | 813 | 11 | 32 | 109 | 203 | 89 | 15 |  |  | 28 | 149 | 132 | 45
47.5 | 45 to 50 | 583 | 16 | 42 | 99 | 87 | 32 | 1 |  |  | 1 | 119 | 135 | 51 |  | 47.5 | 45 to 50 | 583 | 16 | 42 | 99 | 87 | 32 | 1 |  |  | 1 | 119 | 135 | 51
42.5 | 40 to 45 | 632 | 44 | 88 | 159 | 29 | 15 |  |  |  |  | 59 | 137 | 101 |  | 42.5 | 40 to 45 | 632 | 44 | 88 | 159 | 29 | 15 |  |  |  |  | 59 | 137 | 101
37.5 | 35 to 40 | 756 | 166 | 159 | 146 | 26 | 1 |  |  |  |  | 42 | 87 | 129 |  | 37.5 | 35 to 40 | 756 | 166 | 159 | 146 | 26 | 1 |  |  |  |  | 42 | 87 | 129
32.5 | 30 to 35 | 540 | 176 | 126 | 48 | 6 | [5 empty] | 10 | 43 | 131 |  | 32.5 | 30 to 35 | 540 | 176 | 126 | 48 | 6 | [5 empty] | 10 | 43 | 131
27.5 | 25 to 30 | 336 | 144 | 69 | 27 | [7 empty] | 11 | 85 |  | 27.5 | 25 to 30 | 336 | 144 | 69 | 27 | [7 empty] | 11 | 85
22.5 | 20 to 25 | 214 | 80 | 65 | 5 | [8 empty] | 64 |  | 22.5 | 20 to 25 | 214 | 80 | 65 | 5 | [8 empty] | 64
17.5 | 15 to 20 | 136 | 62 | 37 | 1 | [8 empty] | 36 |  | 17.5 | 15 to 20 | 136 | 62 | 37 | 1 | [8 empty] | 36
12.5 | 10 to 15 | 68 | 21 | 13 | [9 empty] | 34 |  | 12.5 | 10 to 15 | 68 | 21 | 13 | [9 empty] | 34
7.5 | 5 to 10 | 19 | 7 | [10 empty] | 12 |  | 7.5 | 5 to 10 | 19 | 7 | [10 empty] | 12
|  | 8760 | [15 empty] | 8760
0
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! | [13 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! | [13 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! | [13 empty] | Tuesday | #REF! | #REF!
Wednesday | #REF! | #REF! | [13 empty] | Wednesday | #REF! | #REF!
Thursday | #REF! | #REF! | [13 empty] | Thursday | #REF! | #REF!
Friday | #REF! | #REF! | [13 empty] | Friday | #REF! | #REF! |  | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | #REF! | #REF! | [13 empty] | Saturday | #REF! | #REF! |  | 7 | 7 | 7 | 7 | 7 | 7 | 7
[20 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8
[20 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
[20 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
[20 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
[20 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12
[20 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13
[20 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
[20 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15
[20 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16
[20 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17
[20 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
[20 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
[20 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[20 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 4 | [5 empty] | 1 | 2 | 1 | [5 empty] | 97.5 | 95 to 100 | 31 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 94 |  |  |  |  | 12 | 16 | 40 | 26 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 239 |  |  |  |  | 30 | 40 | 88 | 71 | 10 |  |  |  |  | 87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12
82.5 | 80 to 85 | 492 |  |  | 5 |  | 42 | 114 | 133 | 138 | 57 | 3 |  |  |  | 82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24
77.5 | 75 to 80 | 695 |  |  | 7 | 4 | 61 | 143 | 190 | 147 | 119 | 24 |  |  |  | 77.5 | 75 to 80 | 553 |  |  |  | 9 | 65 | 98 | 101 | 120 | 93 | 56 |  | 11
72.5 | 70 to 75 | 753 |  |  | 14 | 23 | 65 | 135 | 186 | 163 | 139 | 26 |  | 2 |  | 72.5 | 70 to 75 | 504 |  | 4 |  | 13 | 64 | 76 | 79 | 135 | 86 | 37 |  | 10
67.5 | 65 to 70 | 762 |  | 4 | 17 | 74 | 121 | 134 | 85 | 128 | 136 | 50 | 7 | 6 |  | 67.5 | 65 to 70 | 500 | 15 | 10 | 6 | 42 | 87 | 47 | 39 | 61 | 108 | 56 | 7 | 22
62.5 | 60 to 65 | 903 |  | 27 | 48 | 120 | 167 | 96 | 20 | 62 | 148 | 106 | 79 | 30 |  | 62.5 | 60 to 65 | 464 | 19 | 24 | 14 | 87 | 71 | 14 | 2 | 21 | 71 | 74 | 33 | 34
57.5 | 55 to 60 | 721 | 17 | 10 | 59 | 148 | 109 | 25 |  | 8 | 82 | 156 | 89 | 18 |  | 57.5 | 55 to 60 | 462 | 10 | 46 | 28 | 114 | 68 | 6 |  | 6 | 30 | 78 | 59 | 17
52.5 | 50 to 55 | 813 | 11 | 32 | 109 | 203 | 89 | 15 |  |  | 28 | 149 | 132 | 45 |  | 52.5 | 50 to 55 | 477 | 17 | 60 | 64 | 71 | 40 |  |  |  | 8 | 67 | 88 | 62
47.5 | 45 to 50 | 583 | 16 | 42 | 99 | 87 | 32 | 1 |  |  | 1 | 119 | 135 | 51 |  | 47.5 | 45 to 50 | 332 | 39 | 38 | 67 | 55 | 12 |  |  |  | 2 | 35 | 45 | 39
42.5 | 40 to 45 | 632 | 44 | 88 | 159 | 29 | 15 |  |  |  |  | 59 | 137 | 101 |  | 42.5 | 40 to 45 | 472 | 77 | 39 | 132 | 41 | [5 empty] | 27 | 72 | 84
37.5 | 35 to 40 | 756 | 166 | 159 | 146 | 26 | 1 |  |  |  |  | 42 | 87 | 129 |  | 37.5 | 35 to 40 | 319 | 56 | 33 | 68 | 13 | [5 empty] | 8 | 79 | 62
32.5 | 30 to 35 | 540 | 176 | 126 | 48 | 6 | [5 empty] | 10 | 43 | 131 |  | 32.5 | 30 to 35 | 259 | 65 | 44 | 62 | 5 | [5 empty] | 2 | 38 | 43
27.5 | 25 to 30 | 336 | 144 | 69 | 27 | [7 empty] | 11 | 85 |  | 27.5 | 25 to 30 | 149 | 24 | 53 | 19 | [6 empty] | 1 | 19 | 33
22.5 | 20 to 25 | 214 | 80 | 65 | 5 | [8 empty] | 64 |  | 22.5 | 20 to 25 | 147 | 73 | 26 | 4 | [7 empty] | 8 | 36
17.5 | 15 to 20 | 136 | 62 | 37 | 1 | [8 empty] | 36 |  | 17.5 | 15 to 20 | 100 | 57 | 28 | 1 | [7 empty] | 2 | 12
12.5 | 10 to 15 | 68 | 21 | 13 | [9 empty] | 34 |  | 12.5 | 10 to 15 | 24 | 12 | 12
7.5 | 5 to 10 | 19 | 7 | [10 empty] | 12 |  | 7.5 | 5 to 10 | 4 | 2 | 2
|  | 8760 | [15 empty] | 5475
0
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! | [13 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! | [13 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! | [13 empty] | Tuesday | #REF! | #REF!
Wednesday | #REF! | #REF! | [13 empty] | Wednesday | #REF! | #REF!
Thursday | #REF! | #REF! | [13 empty] | Thursday | #REF! | #REF!
Friday | #REF! | #REF! | [13 empty] | Friday | #REF! | #REF! |  | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | #REF! | #REF! | [13 empty] | Saturday | #REF! | #REF! |  | 7 | 7 | 7 | 7 | 7 | 7 | 7
[20 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8
[20 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
[20 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
[20 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
[20 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12
[20 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13
[20 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
[20 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15
[20 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16
[20 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17
[20 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
[20 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
[20 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 31 | [5 empty] | 11 | 20 | [6 empty] | 97.5 | 95 to 100 | 31 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 191 |  |  |  |  | 7 | 72 | 67 | 33 | 12
82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 415 |  |  |  |  | 51 | 97 | 116 | 87 | 40 | 24
77.5 | 75 to 80 | 570 |  |  |  | 9 | 65 | 99 | 114 | 123 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 553 |  |  |  | 9 | 65 | 98 | 101 | 120 | 93 | 56 |  | 11
72.5 | 70 to 75 | 602 |  | 4 |  | 13 | 66 | 110 | 112 | 159 | 88 | 40 |  | 10 |  | 72.5 | 70 to 75 | 504 |  | 4 |  | 13 | 64 | 76 | 79 | 135 | 86 | 37 |  | 10
67.5 | 65 to 70 | 628 | 16 | 10 | 6 | 42 | 91 | 75 | 75 | 88 | 134 | 59 | 7 | 25 |  | 67.5 | 65 to 70 | 500 | 15 | 10 | 6 | 42 | 87 | 47 | 39 | 61 | 108 | 56 | 7 | 22
62.5 | 60 to 65 | 556 | 21 | 24 | 14 | 91 | 97 | 28 | 13 | 37 | 83 | 77 | 33 | 38 |  | 62.5 | 60 to 65 | 464 | 19 | 24 | 14 | 87 | 71 | 14 | 2 | 21 | 71 | 74 | 33 | 34
57.5 | 55 to 60 | 562 | 13 | 49 | 30 | 122 | 85 | 7 |  | 18 | 56 | 94 | 61 | 27 |  | 57.5 | 55 to 60 | 462 | 10 | 46 | 28 | 114 | 68 | 6 |  | 6 | 30 | 78 | 59 | 17
52.5 | 50 to 55 | 604 | 17 | 76 | 67 | 82 | 55 | 10 |  | 11 | 28 | 90 | 102 | 66 |  | 52.5 | 50 to 55 | 477 | 17 | 60 | 64 | 71 | 40 |  |  |  | 8 | 67 | 88 | 62
47.5 | 45 to 50 | 389 | 44 | 46 | 68 | 67 | 24 | 1 |  |  | 3 | 41 | 52 | 43 |  | 47.5 | 45 to 50 | 332 | 39 | 38 | 67 | 55 | 12 |  |  |  | 2 | 35 | 45 | 39
42.5 | 40 to 45 | 604 | 92 | 47 | 161 | 63 | 13 | 1 |  |  | 3 | 48 | 78 | 98 |  | 42.5 | 40 to 45 | 472 | 77 | 39 | 132 | 41 | [5 empty] | 27 | 72 | 84
37.5 | 35 to 40 | 443 | 68 | 43 | 84 | 41 | 4 |  |  |  |  | 20 | 103 | 80 |  | 37.5 | 35 to 40 | 319 | 56 | 33 | 68 | 13 | [5 empty] | 8 | 79 | 62
32.5 | 30 to 35 | 338 | 76 | 50 | 88 | 7 | [5 empty] | 6 | 53 | 58 |  | 32.5 | 30 to 35 | 259 | 65 | 44 | 62 | 5 | [5 empty] | 2 | 38 | 43
27.5 | 25 to 30 | 188 | 35 | 59 | 23 | 3 | [5 empty] | 3 | 31 | 34 |  | 27.5 | 25 to 30 | 149 | 24 | 53 | 19 | [6 empty] | 1 | 19 | 33
22.5 | 20 to 25 | 191 | 83 | 32 | 11 | [7 empty] | 18 | 47 |  | 22.5 | 20 to 25 | 147 | 73 | 26 | 4 | [7 empty] | 8 | 36
17.5 | 15 to 20 | 136 | 66 | 41 | 6 | [7 empty] | 2 | 21 |  | 17.5 | 15 to 20 | 100 | 57 | 28 | 1 | [7 empty] | 2 | 12
12.5 | 10 to 15 | 41 | 26 | 15 | [11 empty] | 12.5 | 10 to 15 | 24 | 12 | 12
7.5 | 5 to 10 | 9 | 3 | 6 | [11 empty] | 7.5 | 5 to 10 | 4 | 2 | 2
|  | 6570 | [15 empty] | 5475
0
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | #REF! | #REF! |  | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | #REF! | #REF! |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | #REF! | #REF! |  | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | #REF! | #REF! |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | #REF! | #REF! |  | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | #REF! | #REF! |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | #REF! | #REF! |  | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | #REF! | #REF! |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | #REF! | #REF! |  | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
|  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [9 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [9 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
|  |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [9 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [9 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16
|  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17
|  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [9 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 4 | [5 empty] | 1 | 2 | 1 | [5 empty] | 97.5 | 95 to 100 | 1 | [6 empty] | 1
92.5 | 90 to 95 | 73 |  |  |  |  | 12 | 16 | 27 | 18 | [5 empty] | 92.5 | 90 to 95 | 58 |  |  |  |  | 10 | 12 | 21 | 15
87.5 | 85 to 90 | 172 |  |  |  |  | 28 | 30 | 64 | 43 | 7 |  |  |  |  | 87.5 | 85 to 90 | 127 |  |  |  |  | 20 | 24 | 45 | 32 | 6
82.5 | 80 to 85 | 268 |  |  | 4 |  | 28 | 77 | 50 | 68 | 38 | 3 |  |  |  | 82.5 | 80 to 85 | 211 |  |  | 2 |  | 25 | 56 | 43 | 51 | 31 | 3
77.5 | 75 to 80 | 295 |  |  | 6 | 4 | 34 | 62 | 58 | 52 | 61 | 18 |  |  |  | 77.5 | 75 to 80 | 208 |  |  | 5 | 3 | 23 | 47 | 33 | 41 | 41 | 15
72.5 | 70 to 75 | 216 |  |  | 9 | 19 | 22 | 30 | 31 | 42 | 45 | 16 |  | 2 |  | 72.5 | 70 to 75 | 133 |  |  | 6 | 13 | 14 | 18 | 14 | 22 | 32 | 12 |  | 2
67.5 | 65 to 70 | 242 |  | 4 | 5 | 43 | 37 | 25 | 20 | 33 | 52 | 17 | 1 | 5 |  | 67.5 | 65 to 70 | 153 |  | 2 | 5 | 34 | 22 | 11 | 11 | 17 | 36 | 11 | 1 | 3
62.5 | 60 to 65 | 295 |  | 15 | 23 | 52 | 58 | 16 |  | 18 | 32 | 36 | 37 | 8 |  | 62.5 | 60 to 65 | 192 |  | 13 | 15 | 38 | 41 | 7 |  | 6 | 18 | 25 | 24 | 5
57.5 | 55 to 60 | 263 | 5 | 8 | 31 | 39 | 32 | 5 |  | 1 | 13 | 75 | 44 | 10 |  | 57.5 | 55 to 60 | 172 | 2 | 5 | 22 | 26 | 19 | 1 |  |  | 4 | 52 | 33 | 8
52.5 | 50 to 55 | 266 | 4 | 22 | 46 | 53 | 12 | 2 |  |  | 3 | 45 | 61 | 18 |  | 52.5 | 50 to 55 | 182 | 3 | 16 | 36 | 34 | 4 |  |  |  |  | 30 | 45 | 14
47.5 | 45 to 50 | 198 | 7 | 14 | 37 | 19 | 12 |  |  |  | 1 | 29 | 57 | 22 |  | 47.5 | 45 to 50 | 129 | 7 | 9 | 23 | 9 | 6 |  |  |  |  | 19 | 41 | 15
42.5 | 40 to 45 | 203 | 21 | 33 | 58 | 6 | 1 |  |  |  |  | 15 | 36 | 33 |  | 42.5 | 40 to 45 | 135 | 14 | 24 | 43 | 2 | [5 empty] | 7 | 21 | 24
37.5 | 35 to 40 | 217 | 54 | 58 | 37 | 3 | [5 empty] | 6 | 18 | 41 |  | 37.5 | 35 to 40 | 137 | 38 | 39 | 21 | 1 | [5 empty] | 2 | 9 | 27
32.5 | 30 to 35 | 139 | 57 | 25 | 14 | 2 | [5 empty] | 4 | 7 | 30 |  | 32.5 | 30 to 35 | 79 | 39 | 15 | 6 | [7 empty] | 2 | 17
27.5 | 25 to 30 | 106 | 57 | 18 | 5 | [7 empty] | 3 | 23 |  | 27.5 | 25 to 30 | 67 | 36 | 14 | [9 empty] | 17
22.5 | 20 to 25 | 73 | 24 | 21 | 1 | [8 empty] | 27 |  | 22.5 | 20 to 25 | 43 | 16 | 11 | [9 empty] | 16
17.5 | 15 to 20 | 49 | 18 | 15 | [9 empty] | 16 |  | 17.5 | 15 to 20 | 34 | 14 | 9 | [9 empty] | 11
12.5 | 10 to 15 | 33 | 14 | 7 | [9 empty] | 12 |  | 12.5 | 10 to 15 | 17 | 6 | 3 | [9 empty] | 8
7.5 | 5 to 10 | 8 | 3 | [10 empty] | 5 |  | 7.5 | 5 to 10 | 2 | 1 | [10 empty] | 1
|  | 3120 | [15 empty] | 2080
0
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! | [13 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! | [13 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | #REF! | #REF! |  | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | #REF! | #REF! |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | #REF! | #REF! |  | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | #REF! | #REF! |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | #REF! | #REF! |  | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | #REF! | #REF! |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [5 empty] | Friday | #REF! | #REF! |  | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | #REF! | #REF! |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [5 empty] | Saturday | #REF! | #REF! |  | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [9 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11
|  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [9 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | [9 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
|  |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [9 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [9 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16
|  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17
|  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [9 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 1 | [6 empty] | 1 | [6 empty] | 97.5 | 95 to 100 | 1 | [6 empty] | 1
92.5 | 90 to 95 | 58 |  |  |  |  | 10 | 12 | 21 | 15 | [5 empty] | 92.5 | 90 to 95 | 58 |  |  |  |  | 10 | 12 | 21 | 15
87.5 | 85 to 90 | 127 |  |  |  |  | 20 | 24 | 45 | 32 | 6 |  |  |  |  | 87.5 | 85 to 90 | 127 |  |  |  |  | 20 | 24 | 45 | 32 | 6
82.5 | 80 to 85 | 211 |  |  | 2 |  | 25 | 56 | 43 | 51 | 31 | 3 |  |  |  | 82.5 | 80 to 85 | 211 |  |  | 2 |  | 25 | 56 | 43 | 51 | 31 | 3
77.5 | 75 to 80 | 208 |  |  | 5 | 3 | 23 | 47 | 33 | 41 | 41 | 15 |  |  |  | 77.5 | 75 to 80 | 208 |  |  | 5 | 3 | 23 | 47 | 33 | 41 | 41 | 15
72.5 | 70 to 75 | 133 |  |  | 6 | 13 | 14 | 18 | 14 | 22 | 32 | 12 |  | 2 |  | 72.5 | 70 to 75 | 133 |  |  | 6 | 13 | 14 | 18 | 14 | 22 | 32 | 12 |  | 2
67.5 | 65 to 70 | 153 |  | 2 | 5 | 34 | 22 | 11 | 11 | 17 | 36 | 11 | 1 | 3 |  | 67.5 | 65 to 70 | 153 |  | 2 | 5 | 34 | 22 | 11 | 11 | 17 | 36 | 11 | 1 | 3
62.5 | 60 to 65 | 192 |  | 13 | 15 | 38 | 41 | 7 |  | 6 | 18 | 25 | 24 | 5 |  | 62.5 | 60 to 65 | 192 |  | 13 | 15 | 38 | 41 | 7 |  | 6 | 18 | 25 | 24 | 5
57.5 | 55 to 60 | 172 | 2 | 5 | 22 | 26 | 19 | 1 |  |  | 4 | 52 | 33 | 8 |  | 57.5 | 55 to 60 | 172 | 2 | 5 | 22 | 26 | 19 | 1 |  |  | 4 | 52 | 33 | 8
52.5 | 50 to 55 | 182 | 3 | 16 | 36 | 34 | 4 |  |  |  |  | 30 | 45 | 14 |  | 52.5 | 50 to 55 | 182 | 3 | 16 | 36 | 34 | 4 |  |  |  |  | 30 | 45 | 14
47.5 | 45 to 50 | 129 | 7 | 9 | 23 | 9 | 6 |  |  |  |  | 19 | 41 | 15 |  | 47.5 | 45 to 50 | 129 | 7 | 9 | 23 | 9 | 6 |  |  |  |  | 19 | 41 | 15
42.5 | 40 to 45 | 135 | 14 | 24 | 43 | 2 | [5 empty] | 7 | 21 | 24 |  | 42.5 | 40 to 45 | 135 | 14 | 24 | 43 | 2 | [5 empty] | 7 | 21 | 24
37.5 | 35 to 40 | 137 | 38 | 39 | 21 | 1 | [5 empty] | 2 | 9 | 27 |  | 37.5 | 35 to 40 | 137 | 38 | 39 | 21 | 1 | [5 empty] | 2 | 9 | 27
32.5 | 30 to 35 | 79 | 39 | 15 | 6 | [7 empty] | 2 | 17 |  | 32.5 | 30 to 35 | 79 | 39 | 15 | 6 | [7 empty] | 2 | 17
27.5 | 25 to 30 | 67 | 36 | 14 | [9 empty] | 17 |  | 27.5 | 25 to 30 | 67 | 36 | 14 | [9 empty] | 17
22.5 | 20 to 25 | 43 | 16 | 11 | [9 empty] | 16 |  | 22.5 | 20 to 25 | 43 | 16 | 11 | [9 empty] | 16
17.5 | 15 to 20 | 34 | 14 | 9 | [9 empty] | 11 |  | 17.5 | 15 to 20 | 34 | 14 | 9 | [9 empty] | 11
12.5 | 10 to 15 | 17 | 6 | 3 | [9 empty] | 8 |  | 12.5 | 10 to 15 | 17 | 6 | 3 | [9 empty] | 8
7.5 | 5 to 10 | 2 | 1 | [10 empty] | 1 |  | 7.5 | 5 to 10 | 2 | 1 | [10 empty] | 1
|  | 2080 | [15 empty] | 2080
6
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! | [13 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! | [13 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! | [13 empty] | Tuesday | #REF! | #REF!
Wednesday | #REF! | #REF! | [13 empty] | Wednesday | #REF! | #REF!
Thursday | #REF! | #REF! | [13 empty] | Thursday | #REF! | #REF!
Friday | #REF! | #REF! | [13 empty] | Friday | #REF! | #REF!
Saturday | #REF! | #REF! | [13 empty] | Saturday | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 1 | [6 empty] | 1 | [6 empty] | 97.5 | 95 to 100 | 1 | [6 empty] | 1
92.5 | 90 to 95 | 58 |  |  |  |  | 10 | 12 | 21 | 15 | [5 empty] | 92.5 | 90 to 95 | 58 |  |  |  |  | 10 | 12 | 21 | 15
87.5 | 85 to 90 | 127 |  |  |  |  | 20 | 24 | 45 | 32 | 6 |  |  |  |  | 87.5 | 85 to 90 | 127 |  |  |  |  | 20 | 24 | 45 | 32 | 6
82.5 | 80 to 85 | 211 |  |  | 2 |  | 25 | 56 | 43 | 51 | 31 | 3 |  |  |  | 82.5 | 80 to 85 | 211 |  |  | 2 |  | 25 | 56 | 43 | 51 | 31 | 3
77.5 | 75 to 80 | 208 |  |  | 5 | 3 | 23 | 47 | 33 | 41 | 41 | 15 |  |  |  | 77.5 | 75 to 80 | 208 |  |  | 5 | 3 | 23 | 47 | 33 | 41 | 41 | 15
72.5 | 70 to 75 | 133 |  |  | 6 | 13 | 14 | 18 | 14 | 22 | 32 | 12 |  | 2 |  | 72.5 | 70 to 75 | 133 |  |  | 6 | 13 | 14 | 18 | 14 | 22 | 32 | 12 |  | 2
67.5 | 65 to 70 | 153 |  | 2 | 5 | 34 | 22 | 11 | 11 | 17 | 36 | 11 | 1 | 3 |  | 67.5 | 65 to 70 | 153 |  | 2 | 5 | 34 | 22 | 11 | 11 | 17 | 36 | 11 | 1 | 3
62.5 | 60 to 65 | 192 |  | 13 | 15 | 38 | 41 | 7 |  | 6 | 18 | 25 | 24 | 5 |  | 62.5 | 60 to 65 | 192 |  | 13 | 15 | 38 | 41 | 7 |  | 6 | 18 | 25 | 24 | 5
57.5 | 55 to 60 | 172 | 2 | 5 | 22 | 26 | 19 | 1 |  |  | 4 | 52 | 33 | 8 |  | 57.5 | 55 to 60 | 172 | 2 | 5 | 22 | 26 | 19 | 1 |  |  | 4 | 52 | 33 | 8
52.5 | 50 to 55 | 182 | 3 | 16 | 36 | 34 | 4 |  |  |  |  | 30 | 45 | 14 |  | 52.5 | 50 to 55 | 182 | 3 | 16 | 36 | 34 | 4 |  |  |  |  | 30 | 45 | 14
47.5 | 45 to 50 | 129 | 7 | 9 | 23 | 9 | 6 |  |  |  |  | 19 | 41 | 15 |  | 47.5 | 45 to 50 | 129 | 7 | 9 | 23 | 9 | 6 |  |  |  |  | 19 | 41 | 15
42.5 | 40 to 45 | 135 | 14 | 24 | 43 | 2 | [5 empty] | 7 | 21 | 24 |  | 42.5 | 40 to 45 | 135 | 14 | 24 | 43 | 2 | [5 empty] | 7 | 21 | 24
37.5 | 35 to 40 | 137 | 38 | 39 | 21 | 1 | [5 empty] | 2 | 9 | 27 |  | 37.5 | 35 to 40 | 137 | 38 | 39 | 21 | 1 | [5 empty] | 2 | 9 | 27
32.5 | 30 to 35 | 79 | 39 | 15 | 6 | [7 empty] | 2 | 17 |  | 32.5 | 30 to 35 | 79 | 39 | 15 | 6 | [7 empty] | 2 | 17
27.5 | 25 to 30 | 67 | 36 | 14 | [9 empty] | 17 |  | 27.5 | 25 to 30 | 67 | 36 | 14 | [9 empty] | 17
22.5 | 20 to 25 | 43 | 16 | 11 | [9 empty] | 16 |  | 22.5 | 20 to 25 | 43 | 16 | 11 | [9 empty] | 16
17.5 | 15 to 20 | 34 | 14 | 9 | [9 empty] | 11 |  | 17.5 | 15 to 20 | 34 | 14 | 9 | [9 empty] | 11
12.5 | 10 to 15 | 17 | 6 | 3 | [9 empty] | 8 |  | 12.5 | 10 to 15 | 17 | 6 | 3 | [9 empty] | 8
7.5 | 5 to 10 | 2 | 1 | [10 empty] | 1 |  | 7.5 | 5 to 10 | 2 | 1 | [10 empty] | 1
|  | 2080 | [15 empty] | 2080
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | #REF! | #REF! | [13 empty] | Sunday | #REF! | #REF!
Monday | #REF! | #REF! | [13 empty] | Monday | #REF! | #REF!
Tuesday | #REF! | #REF! | [13 empty] | Tuesday | #REF! | #REF!
Wednesday | #REF! | #REF! | [13 empty] | Wednesday | #REF! | #REF!
Thursday | #REF! | #REF! | [13 empty] | Thursday | #REF! | #REF!
Friday | #REF! | #REF! | [13 empty] | Friday | #REF! | #REF!
Saturday | #REF! | #REF! | [13 empty] | Saturday | #REF! | #REF!
|  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [9 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 1 | [6 empty] | 1 | [6 empty] | 97.5 | 95 to 100 | 1 | [6 empty] | 1
92.5 | 90 to 95 | 58 |  |  |  |  | 10 | 12 | 21 | 15 | [5 empty] | 92.5 | 90 to 95 | 58 |  |  |  |  | 10 | 12 | 21 | 15
87.5 | 85 to 90 | 127 |  |  |  |  | 20 | 24 | 45 | 32 | 6 |  |  |  |  | 87.5 | 85 to 90 | 127 |  |  |  |  | 20 | 24 | 45 | 32 | 6
82.5 | 80 to 85 | 211 |  |  | 2 |  | 25 | 56 | 43 | 51 | 31 | 3 |  |  |  | 82.5 | 80 to 85 | 211 |  |  | 2 |  | 25 | 56 | 43 | 51 | 31 | 3
77.5 | 75 to 80 | 208 |  |  | 5 | 3 | 23 | 47 | 33 | 41 | 41 | 15 |  |  |  | 77.5 | 75 to 80 | 208 |  |  | 5 | 3 | 23 | 47 | 33 | 41 | 41 | 15
72.5 | 70 to 75 | 133 |  |  | 6 | 13 | 14 | 18 | 14 | 22 | 32 | 12 |  | 2 |  | 72.5 | 70 to 75 | 133 |  |  | 6 | 13 | 14 | 18 | 14 | 22 | 32 | 12 |  | 2
67.5 | 65 to 70 | 153 |  | 2 | 5 | 34 | 22 | 11 | 11 | 17 | 36 | 11 | 1 | 3 |  | 67.5 | 65 to 70 | 153 |  | 2 | 5 | 34 | 22 | 11 | 11 | 17 | 36 | 11 | 1 | 3
62.5 | 60 to 65 | 192 |  | 13 | 15 | 38 | 41 | 7 |  | 6 | 18 | 25 | 24 | 5 |  | 62.5 | 60 to 65 | 192 |  | 13 | 15 | 38 | 41 | 7 |  | 6 | 18 | 25 | 24 | 5
57.5 | 55 to 60 | 172 | 2 | 5 | 22 | 26 | 19 | 1 |  |  | 4 | 52 | 33 | 8 |  | 57.5 | 55 to 60 | 172 | 2 | 5 | 22 | 26 | 19 | 1 |  |  | 4 | 52 | 33 | 8
52.5 | 50 to 55 | 182 | 3 | 16 | 36 | 34 | 4 |  |  |  |  | 30 | 45 | 14 |  | 52.5 | 50 to 55 | 182 | 3 | 16 | 36 | 34 | 4 |  |  |  |  | 30 | 45 | 14
47.5 | 45 to 50 | 129 | 7 | 9 | 23 | 9 | 6 |  |  |  |  | 19 | 41 | 15 |  | 47.5 | 45 to 50 | 129 | 7 | 9 | 23 | 9 | 6 |  |  |  |  | 19 | 41 | 15
42.5 | 40 to 45 | 135 | 14 | 24 | 43 | 2 | [5 empty] | 7 | 21 | 24 |  | 42.5 | 40 to 45 | 135 | 14 | 24 | 43 | 2 | [5 empty] | 7 | 21 | 24
37.5 | 35 to 40 | 137 | 38 | 39 | 21 | 1 | [5 empty] | 2 | 9 | 27 |  | 37.5 | 35 to 40 | 137 | 38 | 39 | 21 | 1 | [5 empty] | 2 | 9 | 27
32.5 | 30 to 35 | 79 | 39 | 15 | 6 | [7 empty] | 2 | 17 |  | 32.5 | 30 to 35 | 79 | 39 | 15 | 6 | [7 empty] | 2 | 17
27.5 | 25 to 30 | 67 | 36 | 14 | [9 empty] | 17 |  | 27.5 | 25 to 30 | 67 | 36 | 14 | [9 empty] | 17
22.5 | 20 to 25 | 43 | 16 | 11 | [9 empty] | 16 |  | 22.5 | 20 to 25 | 43 | 16 | 11 | [9 empty] | 16
17.5 | 15 to 20 | 34 | 14 | 9 | [9 empty] | 11 |  | 17.5 | 15 to 20 | 34 | 14 | 9 | [9 empty] | 11
12.5 | 10 to 15 | 17 | 6 | 3 | [9 empty] | 8 |  | 12.5 | 10 to 15 | 17 | 6 | 3 | [9 empty] | 8
7.5 | 5 to 10 | 2 | 1 | [10 empty] | 1 |  | 7.5 | 5 to 10 | 2 | 1 | [10 empty] | 1
|  | 2080 | [15 empty] | 2080

## TMY3 DATA (Unoccupied -HVAC) (hidden)
VAV UNOCCUPIED SCHEDULE
UNOCCUPIED (RTU)
|  | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Baseline Equivalent Full Load Hours (%) at Each Bin | Baseline Equivalent Full Load Hours (%) at Each Bin
|  | RTU 1 | RTU 2 | RTU 3 | RTU 4 | RTU 5 | RTU 6 | RTU 7 | RTU 8 | RTU 9 | RTU 10 | RTU 11 | #REF! | [19 empty] | PROPOSED | [20 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Percent % | Percent % | [38 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2
97.5 | 95 to 100 | 0 | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | [17 empty] | RTU 1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  | RTU 7 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3
92.5 | 90 to 95 | 0 | 2 | 47 | 47 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0% | 0% | [17 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4
87.5 | 85 to 90 | 0 | 5 | 116 | 116 | 0 | 0 | 0 | 2 | 5 | 2 | 2 | 2 | 0% | 0% | [17 empty] | Stop | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 |  | Stop | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 |  |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5
82.5 | 80 to 85 | 3 | 22 | 228 | 228 | 5 | 2 | 3 | 11 | 22 | 11 | 11 | 10 | 0% | 0% | [38 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6
77.5 | 75 to 80 | 72 | 118 | 359 | 359 | 82 | 65 | 72 | 105 | 118 | 105 | 105 | 90 | 0% | 0% | [17 empty] | RTU 2 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  | RTU 8 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  |  |  |  | 7 | 7 | 7 | 7 | 7 | 7 | 7
72.5 | 70 to 75 | 242 | 323 | 542 | 542 | 265 | 227 | 242 | 323 | 323 | 323 | 323 | 288 | 0% | 0% | [17 empty] | Start | 600 | 900 | 600 | 900 | 600 | 600 | 600 |  | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
67.5 | 65 to 70 | 291 | 366 | 549 | 549 | 315 | 276 | 291 | 378 | 366 | 378 | 378 | 348 | 0% | 0% | [17 empty] | Stop | 2300 | 1700 | 2200 | 1700 | 2200 | 2300 | 2300 |  | Stop | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  |  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
62.5 | 60 to 65 | 245 | 304 | 410 | 410 | 273 | 224 | 245 | 331 | 304 | 331 | 331 | 291 | 0% | 0% | [38 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
57.5 | 55 to 60 | 247 | 320 | 360 | 360 | 264 | 237 | 247 | 302 | 320 | 302 | 302 | 281 | 4.762% | 0% | [16 empty] | Summer Schedule | RTU 3 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  | RTU 9 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11
52.5 | 50 to 55 | 239 | 303 | 332 | 332 | 255 | 225 | 239 | 303 | 303 | 303 | 303 | 285 | 14.29% | 5.263% | [17 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  | Start | 600 | 900 | 600 | 900 | 600 | 600 | 600 |  |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
47.5 | 45 to 50 | 177 | 210 | 224 | 224 | 194 | 166 | 177 | 232 | 210 | 232 | 232 | 214 | 23.81% | 15.79% | [17 empty] | Stop | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 |  | Stop | 2300 | 1700 | 2200 | 1700 | 2200 | 2300 | 2300 |  |  |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
42.5 | 40 to 45 | 296 | 356 | 349 | 349 | 318 | 278 | 296 | 385 | 356 | 385 | 385 | 332 | 33.33% | 26.32% | [38 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
37.5 | 35 to 40 | 260 | 301 | 291 | 291 | 277 | 243 | 260 | 316 | 301 | 316 | 316 | 287 | 42.86% | 36.84% | [16 empty] | Winter Schedule | RTU 3 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  | RTU 10 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  |  |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
32.5 | 30 to 35 | 173 | 235 | 201 | 201 | 185 | 167 | 173 | 206 | 235 | 206 | 206 | 195 | 52.38% | 47.37% | [17 empty] | Start | 1200 | 600 | 600 | 600 | 600 | 600 | 600 |  | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
27.5 | 25 to 30 | 105 | 128 | 112 | 112 | 112 | 97 | 105 | 137 | 128 | 137 | 137 | 122 | 61.9% | 57.89% | [17 empty] | Stop | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 |  | Stop | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
22.5 | 20 to 25 | 103 | 111 | 116 | 116 | 110 | 96 | 103 | 126 | 111 | 126 | 126 | 113 | 71.43% | 68.42% | [38 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
17.5 | 15 to 20 | 58 | 77 | 67 | 67 | 63 | 56 | 58 | 77 | 77 | 77 | 77 | 71 | 80.95% | 78.95% | [16 empty] | Summer Schedule | RTU 4 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  | RTU 11 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19
12.5 | 10 to 15 | 35 | 39 | 39 | 39 | 36 | 30 | 35 | 42 | 39 | 42 | 42 | 32 | 90.48% | 89.47% | [17 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20
7.5 | 5 to 10 | 9 | 10 | 12 | 12 | 9 | 9 | 9 | 9 | 10 | 9 | 9 | 9 | 100% | 100% | [17 empty] | Stop | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 |  | Stop | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | 2555 | 3230 | 4373 | 4373 | 2763 | 2398 | 2555 | 3285 | 3230 | 3285 | 3285 | 2970 | [40 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | 2555 | 3230 | 4373 | 4373 | 2763 | 2398 | 2555 | 3285 | 3230 | 3285 | 3285 | 2970 | [18 empty] | Winter Schedule | RTU 4 | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  | #REF! | Sun | Mon | Tue | Wed | Thu | Fri | Sat |  |  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | [19 empty] | Start | 1200 | 600 | 600 | 600 | 600 | 600 | 600 |  | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24
[33 empty] | Stop | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 |  | Stop | 2300 | 2000 | 2000 | 2000 | 2000 | 2000 | 2300
Exiting Temperatures |  |  |  | Proposed temperatues |  |  |  |  | TOTAL OCCUPANCY + UNOCCUPANCY
OAT | EFLCH % | EFLHH % |  | OAT | EFLCH % | EFLHH % |  |  | RTU 1 | RTU 2 | RTU 3 | RTU 4 | RTU 5 | RTU 6 | RTU 7 | RTU 8 | RTU 9 | RTU 10 | RTU 11 | #REF! | [12 empty] | RTU 5 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
100 | 0% |  |  | 100 | 0% |  |  | Unoccupied | 2555 | 3230 | 4373 | 4373 | 2763 | 2398 | 2555 | 3285 | 3230 | 3285 | 3285 | 2970 | [12 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600
60 | 0% |  |  | 55 | 0% |  |  | Occupied | 7664 | 7664 | 5009 | 5009 | 5009 | 7664 | 7664 | 5839 | 7664 | 7664 | 2982 | 7664 | [12 empty] | Stop | 2200 | 2100 | 2100 | 2100 | 2100 | 2200 | 2200
60 |  | 0% |  | 55 |  | 0% |  | TOTAL HOURS | 10219 | 10894 | 9382 | 9382 | 7772 | 10062 | 10219 | 9124 | 10894 | 10949 | 6267 | 10634
7.5 |  | 100% |  | 7.5 |  | 100% |  |  | -1459 | -2134 | -622 | -622 | 988 | -1302 | -1459 | -364 | -2134 | -2189 | 2493 | -1874 | [12 empty] | RTU 6 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Slope | 0 | -0.019048 |  | Slope | 0 | -0.021053 | [26 empty] | Start | 600 | 600 | 600 | 600 | 600 | 600 | 600
Intercept | 0 | 1.1429 |  | Intercept | 0 | 1.1579 | [26 empty] | Stop | 2300 | 2200 | 2200 | 2200 | 2200 | 2300 | 2300
Conventional Binning :Conventional Bins for BALTIMORE BLT-WASHNGTN INT'L MD USFA #: 724060TY
BALTIMORE BLT-WASHNGTN INT'L, MD; USAF#: 724060TY; Altitude: 45 meters / 148 ft; Latitude: 39.167; Longitude: -76.683
Units: | I-P | 724060TY | BALTIMORE BLT-WASHNGTN INT'L, MD |  |  | 39.167 | -76.683 | 147.6378 ft
RTU 1 | [65 empty] | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [45 empty] | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [39 empty] | Start | 300 | 300 | 300 | 300 | 300 | 300 | 300
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [39 empty] | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[20 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90
[16 empty] | 82.5 | 80 to 85 | 3 | [6 empty] | 3
[16 empty] | 77.5 | 75 to 80 | 72 |  |  |  |  | 1 | 11 | 45 | 15
[16 empty] | 72.5 | 70 to 75 | 242 |  |  |  |  | 5 | 77 | 81 | 63 | 11 | 5
[16 empty] | 67.5 | 65 to 70 | 291 | 3 |  |  |  | 21 | 62 | 65 | 61 | 54 | 15 | 3 | 7
[16 empty] | 62.5 | 60 to 65 | 245 | 10 | 3 |  | 8 | 61 | 29 | 23 | 34 | 50 | 17 | 2 | 8
[16 empty] | 57.5 | 55 to 60 | 247 | 1 | 12 | 7 | 18 | 39 | 10 |  | 31 | 56 | 40 | 5 | 28
[16 empty] | 52.5 | 50 to 55 | 239 | 1 | 39 | 1 | 45 | 29 | 18 |  | 13 | 23 | 43 | 22 | 5
[16 empty] | 47.5 | 45 to 50 | 177 | 13 | 9 | 15 | 38 | 28 | 2 |  |  | 8 | 17 | 26 | 21
[16 empty] | 42.5 | 40 to 45 | 296 | 35 | 18 | 62 | 52 | 25 | 1 |  |  | 8 | 47 | 27 | 21
[16 empty] | 37.5 | 35 to 40 | 260 | 25 | 26 | 52 | 38 | 8 |  |  |  |  | 19 | 46 | 46
[16 empty] | 32.5 | 30 to 35 | 173 | 26 | 15 | 47 | 8 | [5 empty] | 12 | 36 | 29
[16 empty] | 27.5 | 25 to 30 | 105 | 33 | 20 | 12 | 3 | [5 empty] | 2 | 25 | 10
[16 empty] | 22.5 | 20 to 25 | 103 | 26 | 18 | 17 | [7 empty] | 14 | 28
[16 empty] | 17.5 | 15 to 20 | 58 | 16 | 21 | 4 | [7 empty] | 4 | 13
[16 empty] | 12.5 | 10 to 15 | 35 | 28 | 6 | [9 empty] | 1
[16 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 0 | [15 empty] | 2555
RTU 2
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500 |  | 6 |  | 6
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500 |  | 7 |  | 7
[21 empty] | 8 |  | 8
[21 empty] | 18 |  | 18
[21 empty] | 19 |  | 19
[21 empty] | 20 |  | 20
[21 empty] | 21 |  | 21
[21 empty] | 22 |  | 22
[21 empty] | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95 | 2 | [5 empty] | 1 | 1
[16 empty] | 87.5 | 85 to 90 | 5 |  |  |  |  | 1 | 2 | 2
[16 empty] | 82.5 | 80 to 85 | 22 |  |  |  |  | 4 | 5 | 11 | 1 | 1
[16 empty] | 77.5 | 75 to 80 | 118 |  |  |  |  | 5 | 26 | 62 | 23 | 2
[16 empty] | 72.5 | 70 to 75 | 323 |  |  |  |  | 12 | 102 | 102 | 83 | 16 | 8
[16 empty] | 67.5 | 65 to 70 | 366 | 3 |  |  | 2 | 38 | 68 | 75 | 73 | 69 | 22 | 3 | 13
[16 empty] | 62.5 | 60 to 65 | 304 | 9 | 4 | 1 | 11 | 75 | 29 | 22 | 49 | 60 | 32 | 2 | 10
[16 empty] | 57.5 | 55 to 60 | 320 | 4 | 20 | 9 | 38 | 51 | 8 |  | 33 | 66 | 50 | 9 | 32
[16 empty] | 52.5 | 50 to 55 | 303 | 5 | 45 | 12 | 53 | 36 | 17 |  | 15 | 31 | 52 | 27 | 10
[16 empty] | 47.5 | 45 to 50 | 210 | 15 | 11 | 24 | 46 | 31 | 2 |  |  | 7 | 22 | 29 | 23
[16 empty] | 42.5 | 40 to 45 | 356 | 42 | 25 | 74 | 56 | 24 | 1 |  |  | 8 | 57 | 39 | 30
[16 empty] | 37.5 | 35 to 40 | 301 | 31 | 32 | 63 | 40 | 8 |  |  |  |  | 19 | 62 | 46
[16 empty] | 32.5 | 30 to 35 | 235 | 45 | 19 | 57 | 10 | [5 empty] | 13 | 48 | 43
[16 empty] | 27.5 | 25 to 30 | 128 | 37 | 28 | 14 | 4 | [5 empty] | 1 | 32 | 12
[16 empty] | 22.5 | 20 to 25 | 111 | 28 | 22 | 18 | [7 empty] | 15 | 28
[16 empty] | 17.5 | 15 to 20 | 77 | 24 | 26 | 4 | [7 empty] | 4 | 19
[16 empty] | 12.5 | 10 to 15 | 39 | 33 | 6
[16 empty] | 7.5 | 5 to 10 | 10 |  | 8
|  | 0 | [15 empty] | 3230
RTU 3
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS | [14 empty] | SUMMER SCHEDULE | [15 empty] | WINTER SCHEDULE
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [14 empty] | May Jun Jul Aug Sep Oct | [19 empty] | Jan Feb Mar Apr Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [5 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop | [5 empty] | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 100 | [11 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | [6 empty] | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 100 | [11 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | [6 empty] | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 100 | [11 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | [6 empty] | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 600 | [11 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | [6 empty] | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2200 |  | PLEASE CHECK SUMMER AND WINTER SCHEDULE | [9 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | [6 empty] | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 4300 | [11 empty] | Friday |  |  | 4300 | [12 empty] | Friday | [6 empty] | 2500 | 6
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 4300 | [11 empty] | Saturday |  |  | 4300 | [12 empty] | Saturday | [6 empty] | 2500 | 7
8
9
10
11
[35 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
[35 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15
[35 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16
[35 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17
[35 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
[35 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
[35 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
[35 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
[35 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
[35 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [13 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[35 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [13 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total |  |  |  |  | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs |  |  |  |  | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100 | 19 | 0 | 5 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5 | 95 to 100 | 19 |  | 5 | 11 | [10 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95 | 47 | 0 | 21 | 25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5 | 90 to 95 | 47 |  | 21 | 25 | 1 | [9 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90 | 116 | 6 | 42 | 38 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5 | 85 to 90 | 116 | 6 | 42 | 38 | 22 | 8 | [8 empty] | 87.5 | 85 to 90
[16 empty] | 82.5 | 80 to 85 | 228 | 35 | 42 | 64 | 49 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5 | 80 to 85 | 228 | 35 | 42 | 64 | 49 | 24 | 14 | [7 empty] | 82.5 | 80 to 85
[16 empty] | 77.5 | 75 to 80 | 359 | 34 | 65 | 101 | 79 | 53 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5 | 75 to 80 | 359 | 34 | 65 | 101 | 79 | 53 | 27 | [7 empty] | 77.5 | 75 to 80
[16 empty] | 72.5 | 70 to 75 | 542 | 42 | 135 | 137 | 147 | 56 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5 | 70 to 75 | 541 | 42 | 135 | 137 | 147 | 56 | 24 | [7 empty] | 72.5 | 70 to 75 | 1 |  |  |  | 1
[16 empty] | 67.5 | 65 to 70 | 549 | 76 | 103 | 90 | 98 | 124 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5 | 65 to 70 | 535 | 73 | 96 | 90 | 98 | 124 | 54 | [7 empty] | 67.5 | 65 to 70 | 14 | 3 |  |  | 1 | 3 | 7
[16 empty] | 62.5 | 60 to 65 | 410 | 110 | 46 | 27 | 51 | 90 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 62.5 | 60 to 65 | 376 | 108 | 38 | 27 | 51 | 90 | 62 | [7 empty] | 62.5 | 60 to 65 | 34 | 10 | 3 |  | 11 | 2 | 8
[16 empty] | 57.5 | 55 to 60 | 360 | 79 | 43 | 0 | 36 | 75 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5 | 55 to 60 | 279 | 74 | 14 |  | 36 | 75 | 80 | [7 empty] | 57.5 | 55 to 60 | 81 | 3 | 15 | 7 | 22 | 5 | 29
[16 empty] | 52.5 | 50 to 55 | 332 | 82 | 25 | 0 | 13 | 32 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 52.5 | 50 to 55 | 200 | 51 | 19 |  | 13 | 32 | 85 | [7 empty] | 52.5 | 50 to 55 | 132 | 2 | 39 | 2 | 52 | 31 | 6
[16 empty] | 47.5 | 45 to 50 | 224 | 69 | 25 | 0 | 0 | 10 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 47.5 | 45 to 50 | 88 | 39 | 2 |  |  | 10 | 37 | [7 empty] | 47.5 | 45 to 50 | 136 | 13 | 12 | 16 | 42 | 30 | 23
[16 empty] | 42.5 | 40 to 45 | 349 | 56 | 31 | 0 | 0 | 8 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5 | 40 to 45 | 105 | 26 | 1 |  |  | 8 | 70 | [7 empty] | 42.5 | 40 to 45 | 244 | 40 | 19 | 70 | 55 | 30 | 30
[16 empty] | 37.5 | 35 to 40 | 291 | 59 | 48 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5 | 35 to 40 | 34 | 8 |  |  |  |  | 26 | [7 empty] | 37.5 | 35 to 40 | 257 | 29 | 27 | 60 | 42 | 51 | 48
[16 empty] | 32.5 | 30 to 35 | 201 | 39 | 32 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5 | 30 to 35 | 15 | [5 empty] | 15 | [7 empty] | 32.5 | 30 to 35 | 186 | 29 | 22 | 53 | 11 | 39 | 32
[16 empty] | 27.5 | 25 to 30 | 112 | 25 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5 | 25 to 30 | 2 | [5 empty] | 2 | [7 empty] | 27.5 | 25 to 30 | 110 | 37 | 23 | 12 | 3 | 25 | 10
[16 empty] | 22.5 | 20 to 25 | 116 | 14 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 20 to 25 | [14 empty] | 22.5 | 20 to 25 | 116 | 28 | 18 | 17 |  | 14 | 39
[16 empty] | 17.5 | 15 to 20 | 67 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 15 to 20 | [14 empty] | 17.5 | 15 to 20 | 67 | 23 | 22 | 4 |  | 4 | 14
[16 empty] | 12.5 | 10 to 15 | 39 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 10 to 15 | [14 empty] | 12.5 | 10 to 15 | 39 | 30 | 8 |  |  |  | 1
[16 empty] | 7.5 | 5 to 10 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 5 to 10 | [14 empty] | 7.5 | 5 to 10 | 12 |  | 7
|  | 0 | [15 empty] | 4373 | [14 empty] | 2944 | [15 empty] | 1429
RTU 4
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS | [14 empty] | SUMMER SCHEDULE | [15 empty] | WINTER SCHEDULE
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [14 empty] | May Jun Jul Aug Sep Oct | [19 empty] | Jan Feb Mar Apr Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [5 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop | [5 empty] | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 |  |  |  |  | 0 | 0 | 0 | [5 empty] | Sunday |  |  | 100 | [11 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Sunday | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 100 | [11 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | Monday | [7 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 100 | [11 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | Tuesday | [7 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 600 | [11 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [5 empty] | Wednesday | [7 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2200 |  | PLEASE CHECK SUMMER AND WINTER SCHEDULE | [9 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | Thursday | [7 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 4300 | [11 empty] | Friday |  |  | 4300 | [12 empty] | Friday | [7 empty] | 6
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 4300 | [11 empty] | Saturday |  |  | 4300 | [12 empty] | Saturday | [7 empty] | 7
8
9
10
11
[35 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
[35 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15
[35 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16
[35 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17
[35 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
[35 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
[35 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
[35 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
[35 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
[35 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23 | [13 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[35 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [13 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total |  |  |  |  | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs |  |  |  |  | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100 | 19 | 0 | 5 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5 | 95 to 100 | 19 |  | 5 | 11 | [10 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95 | 47 | 0 | 21 | 25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5 | 90 to 95 | 47 |  | 21 | 25 | 1 | [9 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90 | 116 | 6 | 42 | 38 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5 | 85 to 90 | 116 | 6 | 42 | 38 | 22 | 8 | [8 empty] | 87.5 | 85 to 90
[16 empty] | 82.5 | 80 to 85 | 228 | 35 | 42 | 64 | 49 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5 | 80 to 85 | 228 | 35 | 42 | 64 | 49 | 24 | 14 | [7 empty] | 82.5 | 80 to 85
[16 empty] | 77.5 | 75 to 80 | 359 | 34 | 65 | 101 | 79 | 53 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5 | 75 to 80 | 359 | 34 | 65 | 101 | 79 | 53 | 27 | [7 empty] | 77.5 | 75 to 80
[16 empty] | 72.5 | 70 to 75 | 542 | 43 | 135 | 137 | 147 | 56 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5 | 70 to 75 | 541 | 42 | 135 | 137 | 147 | 56 | 24 | [7 empty] | 72.5 | 70 to 75 | 1 |  |  |  | 1
[16 empty] | 67.5 | 65 to 70 | 549 | 87 | 99 | 97 | 98 | 124 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5 | 65 to 70 | 535 | 73 | 96 | 90 | 98 | 124 | 54 | [7 empty] | 67.5 | 65 to 70 | 14 | 3 |  |  | 1 | 3 | 7
[16 empty] | 62.5 | 60 to 65 | 410 | 142 | 40 | 35 | 51 | 90 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 62.5 | 60 to 65 | 376 | 108 | 38 | 27 | 51 | 90 | 62 | [7 empty] | 62.5 | 60 to 65 | 34 | 10 | 3 |  | 11 | 2 | 8
[16 empty] | 57.5 | 55 to 60 | 360 | 155 | 19 | 29 | 36 | 75 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5 | 55 to 60 | 279 | 74 | 14 |  | 36 | 75 | 80 | [7 empty] | 57.5 | 55 to 60 | 81 | 3 | 15 | 7 | 22 | 5 | 29
[16 empty] | 52.5 | 50 to 55 | 332 | 183 | 50 | 6 | 13 | 32 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 52.5 | 50 to 55 | 200 | 51 | 19 |  | 13 | 32 | 85 | [7 empty] | 52.5 | 50 to 55 | 132 | 2 | 39 | 2 | 52 | 31 | 6
[16 empty] | 47.5 | 45 to 50 | 224 | 175 | 32 | 23 | 0 | 10 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 47.5 | 45 to 50 | 88 | 39 | 2 |  |  | 10 | 37 | [7 empty] | 47.5 | 45 to 50 | 136 | 13 | 12 | 16 | 42 | 30 | 23
[16 empty] | 42.5 | 40 to 45 | 349 | 270 | 31 | 30 | 0 | 8 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5 | 40 to 45 | 105 | 26 | 1 |  |  | 8 | 70 | [7 empty] | 42.5 | 40 to 45 | 244 | 40 | 19 | 70 | 55 | 30 | 30
[16 empty] | 37.5 | 35 to 40 | 291 | 265 | 51 | 48 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5 | 35 to 40 | 34 | 8 |  |  |  |  | 26 | [7 empty] | 37.5 | 35 to 40 | 257 | 29 | 27 | 60 | 42 | 51 | 48
[16 empty] | 32.5 | 30 to 35 | 201 | 186 | 39 | 32 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5 | 30 to 35 | 15 | [5 empty] | 15 | [7 empty] | 32.5 | 30 to 35 | 186 | 29 | 22 | 53 | 11 | 39 | 32
[16 empty] | 27.5 | 25 to 30 | 112 | 110 | 25 | 10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5 | 25 to 30 | 2 | [5 empty] | 2 | [7 empty] | 27.5 | 25 to 30 | 110 | 37 | 23 | 12 | 3 | 25 | 10
[16 empty] | 22.5 | 20 to 25 | 116 | 116 | 14 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 20 to 25 | [14 empty] | 22.5 | 20 to 25 | 116 | 28 | 18 | 17 |  | 14 | 39
[16 empty] | 17.5 | 15 to 20 | 67 | 67 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 15 to 20 | [14 empty] | 17.5 | 15 to 20 | 67 | 23 | 22 | 4 |  | 4 | 14
[16 empty] | 12.5 | 10 to 15 | 39 | 39 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 10 to 15 | [14 empty] | 12.5 | 10 to 15 | 39 | 30 | 8 |  |  |  | 1
[16 empty] | 7.5 | 5 to 10 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 5 to 10 | [14 empty] | 7.5 | 5 to 10 | 12 |  | 7
|  | 0 | [15 empty] | 4373 | [14 empty] | 2944 | [15 empty] | 1429
RTU 5
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[21 empty] | 22 | 22 | 22 | 22
[20 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90
[16 empty] | 82.5 | 80 to 85 | 5 | [6 empty] | 5
[16 empty] | 77.5 | 75 to 80 | 82 |  |  |  |  | 3 | 14 | 49 | 16
[16 empty] | 72.5 | 70 to 75 | 265 |  |  |  |  | 5 | 85 | 88 | 71 | 11 | 5
[16 empty] | 67.5 | 65 to 70 | 315 | 3 |  |  |  | 24 | 67 | 68 | 64 | 59 | 19 | 3 | 8
[16 empty] | 62.5 | 60 to 65 | 273 | 11 | 4 |  | 9 | 69 | 30 | 24 | 40 | 54 | 19 | 3 | 10
[16 empty] | 57.5 | 55 to 60 | 264 | 1 | 13 | 8 | 21 | 40 | 10 |  | 32 | 60 | 43 | 6 | 30
[16 empty] | 52.5 | 50 to 55 | 255 | 2 | 42 | 2 | 48 | 31 | 18 |  | 13 | 26 | 46 | 22 | 5
[16 empty] | 47.5 | 45 to 50 | 194 | 13 | 9 | 19 | 43 | 31 | 2 |  |  | 8 | 18 | 28 | 23
[16 empty] | 42.5 | 40 to 45 | 318 | 38 | 21 | 66 | 55 | 25 | 1 |  |  | 8 | 51 | 30 | 23
[16 empty] | 37.5 | 35 to 40 | 277 | 28 | 28 | 56 | 38 | 8 |  |  |  |  | 20 | 52 | 47
[16 empty] | 32.5 | 30 to 35 | 185 | 29 | 16 | 48 | 9 | [5 empty] | 12 | 39 | 32
[16 empty] | 27.5 | 25 to 30 | 112 | 33 | 23 | 13 | 3 | [5 empty] | 2 | 26 | 12
[16 empty] | 22.5 | 20 to 25 | 110 | 30 | 19 | 19 | [7 empty] | 14 | 28
[16 empty] | 17.5 | 15 to 20 | 63 | 18 | 22 | 4 | [7 empty] | 5 | 14
[16 empty] | 12.5 | 10 to 15 | 36 | 29 | 6 | [9 empty] | 1
[16 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 0 | [15 empty] | 2763
RTU 6
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[21 empty] | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90
[16 empty] | 82.5 | 80 to 85 | 2 | [6 empty] | 2
[16 empty] | 77.5 | 75 to 80 | 65 |  |  |  |  | 1 | 10 | 41 | 13
[16 empty] | 72.5 | 70 to 75 | 227 |  |  |  |  | 5 | 74 | 76 | 58 | 9 | 5
[16 empty] | 67.5 | 65 to 70 | 276 | 3 |  |  |  | 19 | 59 | 62 | 58 | 50 | 15 | 3 | 7
[16 empty] | 62.5 | 60 to 65 | 224 | 9 | 2 |  | 8 | 56 | 26 | 22 | 33 | 45 | 14 | 2 | 7
[16 empty] | 57.5 | 55 to 60 | 237 | 1 | 12 | 7 | 16 | 39 | 8 |  | 30 | 54 | 38 | 4 | 28
[16 empty] | 52.5 | 50 to 55 | 225 | 1 | 36 | 1 | 40 | 27 | 17 |  | 13 | 23 | 41 | 22 | 4
[16 empty] | 47.5 | 45 to 50 | 166 | 12 | 9 | 13 | 36 | 27 | 2 |  |  | 7 | 16 | 23 | 21
[16 empty] | 42.5 | 40 to 45 | 278 | 34 | 17 | 57 | 49 | 23 | 1 |  |  | 8 | 45 | 25 | 19
[16 empty] | 37.5 | 35 to 40 | 243 | 22 | 25 | 50 | 37 | 8 |  |  |  |  | 18 | 42 | 41
[16 empty] | 32.5 | 30 to 35 | 167 | 26 | 14 | 45 | 7 | [5 empty] | 11 | 36 | 28
[16 empty] | 27.5 | 25 to 30 | 97 | 30 | 18 | 10 | 3 | [5 empty] | 1 | 25 | 10
[16 empty] | 22.5 | 20 to 25 | 96 | 25 | 18 | 17 | [7 empty] | 12 | 24
[16 empty] | 17.5 | 15 to 20 | 56 | 15 | 20 | 4 | [7 empty] | 4 | 13
[16 empty] | 12.5 | 10 to 15 | 30 | 26 | 4
[16 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 0 | [15 empty] | 2398
RTU 7
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[20 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90
[16 empty] | 82.5 | 80 to 85 | 3 | [6 empty] | 3
[16 empty] | 77.5 | 75 to 80 | 72 |  |  |  |  | 1 | 11 | 45 | 15
[16 empty] | 72.5 | 70 to 75 | 242 |  |  |  |  | 5 | 77 | 81 | 63 | 11 | 5
[16 empty] | 67.5 | 65 to 70 | 291 | 3 |  |  |  | 21 | 62 | 65 | 61 | 54 | 15 | 3 | 7
[16 empty] | 62.5 | 60 to 65 | 245 | 10 | 3 |  | 8 | 61 | 29 | 23 | 34 | 50 | 17 | 2 | 8
[16 empty] | 57.5 | 55 to 60 | 247 | 1 | 12 | 7 | 18 | 39 | 10 |  | 31 | 56 | 40 | 5 | 28
[16 empty] | 52.5 | 50 to 55 | 239 | 1 | 39 | 1 | 45 | 29 | 18 |  | 13 | 23 | 43 | 22 | 5
[16 empty] | 47.5 | 45 to 50 | 177 | 13 | 9 | 15 | 38 | 28 | 2 |  |  | 8 | 17 | 26 | 21
[16 empty] | 42.5 | 40 to 45 | 296 | 35 | 18 | 62 | 52 | 25 | 1 |  |  | 8 | 47 | 27 | 21
[16 empty] | 37.5 | 35 to 40 | 260 | 25 | 26 | 52 | 38 | 8 |  |  |  |  | 19 | 46 | 46
[16 empty] | 32.5 | 30 to 35 | 173 | 26 | 15 | 47 | 8 | [5 empty] | 12 | 36 | 29
[16 empty] | 27.5 | 25 to 30 | 105 | 33 | 20 | 12 | 3 | [5 empty] | 2 | 25 | 10
[16 empty] | 22.5 | 20 to 25 | 103 | 26 | 18 | 17 | [7 empty] | 14 | 28
[16 empty] | 17.5 | 15 to 20 | 58 | 16 | 21 | 4 | [7 empty] | 4 | 13
[16 empty] | 12.5 | 10 to 15 | 35 | 28 | 6 | [9 empty] | 1
[16 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 0 | [15 empty] | 2555
RTU 8
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[20 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
[20 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
[20 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
[20 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 31 | [5 empty] | 8 | 20 | [6 empty] | 97.5 | 95 to 100
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | 2 | [5 empty] | 92.5 | 90 to 95
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12 |  |  |  |  | 87.5 | 85 to 90 | 2 | [6 empty] | 2
82.5 | 80 to 85 | 418 |  |  |  |  | 51 | 97 | 119 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 11 |  |  |  |  | 1 |  | 8 | 2
77.5 | 75 to 80 | 588 |  |  |  | 9 | 67 | 105 | 120 | 127 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 105 |  |  |  |  | 3 | 21 | 61 | 20
72.5 | 70 to 75 | 601 |  | 4 |  | 13 | 65 | 105 | 107 | 165 | 94 | 38 |  | 10 |  | 72.5 | 70 to 75 | 323 |  |  |  |  | 6 | 102 | 103 | 88 | 19 | 5
67.5 | 65 to 70 | 607 | 15 | 10 | 6 | 42 | 97 | 67 | 68 | 80 | 130 | 61 | 7 | 24 |  | 67.5 | 65 to 70 | 378 | 3 |  |  |  | 36 | 76 | 79 | 76 | 72 | 25 | 3 | 8
62.5 | 60 to 65 | 569 | 21 | 27 | 14 | 89 | 101 | 26 | 8 | 36 | 90 | 84 | 34 | 39 |  | 62.5 | 60 to 65 | 331 | 13 | 6 |  | 10 | 81 | 36 | 26 | 45 | 67 | 28 | 4 | 15
57.5 | 55 to 60 | 540 | 13 | 49 | 29 | 125 | 74 | 12 |  | 13 | 49 | 91 | 62 | 23 |  | 57.5 | 55 to 60 | 302 | 2 | 15 | 9 | 32 | 44 | 13 |  | 35 | 65 | 46 | 9 | 32
52.5 | 50 to 55 | 578 | 18 | 74 | 67 | 88 | 55 | 7 |  | 4 | 19 | 85 | 95 | 66 |  | 52.5 | 50 to 55 | 303 | 2 | 51 | 8 | 56 | 36 | 19 |  | 13 | 29 | 55 | 27 | 7
47.5 | 45 to 50 | 394 | 42 | 42 | 76 | 72 | 20 |  |  |  | 5 | 40 | 56 | 41 |  | 47.5 | 45 to 50 | 232 | 15 | 9 | 23 | 54 | 38 | 2 |  |  | 10 | 22 | 33 | 26
42.5 | 40 to 45 | 591 | 88 | 47 | 158 | 61 | 10 |  |  |  | 1 | 43 | 83 | 100 |  | 42.5 | 40 to 45 | 385 | 48 | 29 | 81 | 65 | 26 | 1 |  |  | 8 | 58 | 39 | 30
37.5 | 35 to 40 | 421 | 73 | 41 | 84 | 24 | [5 empty] | 16 | 103 | 80 |  | 37.5 | 35 to 40 | 316 | 34 | 29 | 63 | 39 | 8 |  |  |  |  | 23 | 63 | 57
32.5 | 30 to 35 | 316 | 72 | 49 | 77 | 10 | [5 empty] | 8 | 47 | 53 |  | 32.5 | 30 to 35 | 206 | 32 | 17 | 54 | 11 | [5 empty] | 15 | 41 | 36
27.5 | 25 to 30 | 191 | 35 | 64 | 26 | 1 | [5 empty] | 3 | 24 | 38 |  | 27.5 | 25 to 30 | 137 | 38 | 30 | 18 | 3 | [5 empty] | 2 | 28 | 18
22.5 | 20 to 25 | 185 | 82 | 30 | 9 | [7 empty] | 16 | 48 |  | 22.5 | 20 to 25 | 126 | 35 | 22 | 19 | [7 empty] | 18 | 32
17.5 | 15 to 20 | 123 | 66 | 35 | 2 | [7 empty] | 3 | 17 |  | 17.5 | 15 to 20 | 77 | 27 | 25 | 4 | [7 empty] | 5 | 16
12.5 | 10 to 15 | 45 | 23 | 20 | [9 empty] | 2 |  | 12.5 | 10 to 15 | 42 | 30 | 10 | [9 empty] | 2
7.5 | 5 to 10 | 5 | 1 | 1 | [11 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 6467 | [15 empty] | 3285
RTU 9
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500 |  | 6 |  | 6
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500 |  | 7 |  | 7
[21 empty] | 8 |  | 8
[21 empty] | 18 |  | 18
[21 empty] | 19 |  | 19
[21 empty] | 20 |  | 20
[21 empty] | 21 |  | 21
[21 empty] | 22 |  | 22
[21 empty] | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95 | 2 | [5 empty] | 1 | 1
[16 empty] | 87.5 | 85 to 90 | 5 |  |  |  |  | 1 | 2 | 2
[16 empty] | 82.5 | 80 to 85 | 22 |  |  |  |  | 4 | 5 | 11 | 1 | 1
[16 empty] | 77.5 | 75 to 80 | 118 |  |  |  |  | 5 | 26 | 62 | 23 | 2
[16 empty] | 72.5 | 70 to 75 | 323 |  |  |  |  | 12 | 102 | 102 | 83 | 16 | 8
[16 empty] | 67.5 | 65 to 70 | 366 | 3 |  |  | 2 | 38 | 68 | 75 | 73 | 69 | 22 | 3 | 13
[16 empty] | 62.5 | 60 to 65 | 304 | 9 | 4 | 1 | 11 | 75 | 29 | 22 | 49 | 60 | 32 | 2 | 10
[16 empty] | 57.5 | 55 to 60 | 320 | 4 | 20 | 9 | 38 | 51 | 8 |  | 33 | 66 | 50 | 9 | 32
[16 empty] | 52.5 | 50 to 55 | 303 | 5 | 45 | 12 | 53 | 36 | 17 |  | 15 | 31 | 52 | 27 | 10
[16 empty] | 47.5 | 45 to 50 | 210 | 15 | 11 | 24 | 46 | 31 | 2 |  |  | 7 | 22 | 29 | 23
[16 empty] | 42.5 | 40 to 45 | 356 | 42 | 25 | 74 | 56 | 24 | 1 |  |  | 8 | 57 | 39 | 30
[16 empty] | 37.5 | 35 to 40 | 301 | 31 | 32 | 63 | 40 | 8 |  |  |  |  | 19 | 62 | 46
[16 empty] | 32.5 | 30 to 35 | 235 | 45 | 19 | 57 | 10 | [5 empty] | 13 | 48 | 43
[16 empty] | 27.5 | 25 to 30 | 128 | 37 | 28 | 14 | 4 | [5 empty] | 1 | 32 | 12
[16 empty] | 22.5 | 20 to 25 | 111 | 28 | 22 | 18 | [7 empty] | 15 | 28
[16 empty] | 17.5 | 15 to 20 | 77 | 24 | 26 | 4 | [7 empty] | 4 | 19
[16 empty] | 12.5 | 10 to 15 | 39 | 33 | 6
[16 empty] | 7.5 | 5 to 10 | 10 |  | 8
|  | 0 | [15 empty] | 3230
RTU 10
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[20 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
[20 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
[20 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90 | 2 | [6 empty] | 2
[16 empty] | 82.5 | 80 to 85 | 11 |  |  |  |  | 1 |  | 8 | 2
[16 empty] | 77.5 | 75 to 80 | 105 |  |  |  |  | 3 | 21 | 61 | 20
[16 empty] | 72.5 | 70 to 75 | 323 |  |  |  |  | 6 | 102 | 103 | 88 | 19 | 5
[16 empty] | 67.5 | 65 to 70 | 378 | 3 |  |  |  | 36 | 76 | 79 | 76 | 72 | 25 | 3 | 8
[16 empty] | 62.5 | 60 to 65 | 331 | 13 | 6 |  | 10 | 81 | 36 | 26 | 45 | 67 | 28 | 4 | 15
[16 empty] | 57.5 | 55 to 60 | 302 | 2 | 15 | 9 | 32 | 44 | 13 |  | 35 | 65 | 46 | 9 | 32
[16 empty] | 52.5 | 50 to 55 | 303 | 2 | 51 | 8 | 56 | 36 | 19 |  | 13 | 29 | 55 | 27 | 7
[16 empty] | 47.5 | 45 to 50 | 232 | 15 | 9 | 23 | 54 | 38 | 2 |  |  | 10 | 22 | 33 | 26
[16 empty] | 42.5 | 40 to 45 | 385 | 48 | 29 | 81 | 65 | 26 | 1 |  |  | 8 | 58 | 39 | 30
[16 empty] | 37.5 | 35 to 40 | 316 | 34 | 29 | 63 | 39 | 8 |  |  |  |  | 23 | 63 | 57
[16 empty] | 32.5 | 30 to 35 | 206 | 32 | 17 | 54 | 11 | [5 empty] | 15 | 41 | 36
[16 empty] | 27.5 | 25 to 30 | 137 | 38 | 30 | 18 | 3 | [5 empty] | 2 | 28 | 18
[16 empty] | 22.5 | 20 to 25 | 126 | 35 | 22 | 19 | [7 empty] | 18 | 32
[16 empty] | 17.5 | 15 to 20 | 77 | 27 | 25 | 4 | [7 empty] | 5 | 16
[16 empty] | 12.5 | 10 to 15 | 42 | 30 | 10 | [9 empty] | 2
[16 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 0 | [15 empty] | 3285
RTU 11
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[20 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
[20 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
[20 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90 | 2 | [6 empty] | 2
[16 empty] | 82.5 | 80 to 85 | 11 |  |  |  |  | 1 |  | 8 | 2
[16 empty] | 77.5 | 75 to 80 | 105 |  |  |  |  | 3 | 21 | 61 | 20
[16 empty] | 72.5 | 70 to 75 | 323 |  |  |  |  | 6 | 102 | 103 | 88 | 19 | 5
[16 empty] | 67.5 | 65 to 70 | 378 | 3 |  |  |  | 36 | 76 | 79 | 76 | 72 | 25 | 3 | 8
[16 empty] | 62.5 | 60 to 65 | 331 | 13 | 6 |  | 10 | 81 | 36 | 26 | 45 | 67 | 28 | 4 | 15
[16 empty] | 57.5 | 55 to 60 | 302 | 2 | 15 | 9 | 32 | 44 | 13 |  | 35 | 65 | 46 | 9 | 32
[16 empty] | 52.5 | 50 to 55 | 303 | 2 | 51 | 8 | 56 | 36 | 19 |  | 13 | 29 | 55 | 27 | 7
[16 empty] | 47.5 | 45 to 50 | 232 | 15 | 9 | 23 | 54 | 38 | 2 |  |  | 10 | 22 | 33 | 26
[16 empty] | 42.5 | 40 to 45 | 385 | 48 | 29 | 81 | 65 | 26 | 1 |  |  | 8 | 58 | 39 | 30
[16 empty] | 37.5 | 35 to 40 | 316 | 34 | 29 | 63 | 39 | 8 |  |  |  |  | 23 | 63 | 57
[16 empty] | 32.5 | 30 to 35 | 206 | 32 | 17 | 54 | 11 | [5 empty] | 15 | 41 | 36
[16 empty] | 27.5 | 25 to 30 | 137 | 38 | 30 | 18 | 3 | [5 empty] | 2 | 28 | 18
[16 empty] | 22.5 | 20 to 25 | 126 | 35 | 22 | 19 | [7 empty] | 18 | 32
[16 empty] | 17.5 | 15 to 20 | 77 | 27 | 25 | 4 | [7 empty] | 5 | 16
[16 empty] | 12.5 | 10 to 15 | 42 | 30 | 10 | [9 empty] | 2
[16 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 0 | [15 empty] | 3285
#REF!
EXISTING OPERATING HOURS | [15 empty] | PROPOSED OPERATING HOURS
|  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [15 empty] | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [6 empty] | Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [12 empty] | Sunday |  |  | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 0 | 100 | 100 | [12 empty] | Monday |  |  | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 0 | 100 | 100 | [12 empty] | Tuesday |  |  | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 0 | 100 | 100 | [12 empty] | Wednesday |  |  | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 0 | 100 | 100 | [12 empty] | Thursday |  |  | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 0 | 100 | 100 | [12 empty] | Friday |  |  | 2500
Saturday | 0 | 100 | 100 | [12 empty] | Saturday |  |  | 2500
[21 empty] | 21 | 21 | 21 | 21 | 21
[21 empty] | 22 | 22 | 22 | 22 | 22
[20 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
[20 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
[16 empty] | 97.5 | 95 to 100
[16 empty] | 92.5 | 90 to 95
[16 empty] | 87.5 | 85 to 90 | 2 | [6 empty] | 2
[16 empty] | 82.5 | 80 to 85 | 10 |  |  |  |  | 1 |  | 8 | 1
[16 empty] | 77.5 | 75 to 80 | 90 |  |  |  |  | 3 | 17 | 52 | 18
[16 empty] | 72.5 | 70 to 75 | 288 |  |  |  |  | 6 | 97 | 91 | 76 | 13 | 5
[16 empty] | 67.5 | 65 to 70 | 348 | 3 |  |  |  | 32 | 70 | 72 | 72 | 64 | 24 | 3 | 8
[16 empty] | 62.5 | 60 to 65 | 291 | 13 | 3 |  | 10 | 70 | 29 | 24 | 43 | 60 | 23 | 4 | 12
[16 empty] | 57.5 | 55 to 60 | 281 | 2 | 15 | 9 | 25 | 43 | 12 |  | 32 | 62 | 43 | 6 | 32
[16 empty] | 52.5 | 50 to 55 | 285 | 2 | 48 | 7 | 50 | 34 | 18 |  | 13 | 28 | 52 | 26 | 7
[16 empty] | 47.5 | 45 to 50 | 214 | 14 | 9 | 20 | 51 | 35 | 2 |  |  | 8 | 19 | 31 | 25
[16 empty] | 42.5 | 40 to 45 | 332 | 43 | 24 | 68 | 54 | 23 | 1 |  |  | 8 | 55 | 31 | 25
[16 empty] | 37.5 | 35 to 40 | 287 | 28 | 28 | 59 | 39 | 8 |  |  |  |  | 19 | 56 | 50
[16 empty] | 32.5 | 30 to 35 | 195 | 31 | 17 | 53 | 8 | [5 empty] | 11 | 41 | 34
[16 empty] | 27.5 | 25 to 30 | 122 | 33 | 26 | 16 | 3 | [5 empty] | 1 | 27 | 16
[16 empty] | 22.5 | 20 to 25 | 113 | 33 | 20 | 19 | [7 empty] | 16 | 25
[16 empty] | 17.5 | 15 to 20 | 71 | 22 | 25 | 4 | [7 empty] | 5 | 15
[16 empty] | 12.5 | 10 to 15 | 32 | 28 | 4
[16 empty] | 7.5 | 5 to 10 | 9 |  | 7
|  | 0 | [15 empty] | 2970

## ECM2.3 (hidden)
ECM- |  |  |  | #REF! | #REF!
Input Variables | [5 empty] | Equations & Variables
System Efficiency (Cooling EER) |  |  | See Below |  |  | Energy Equation (Cooling kWh) | =Tons*(12/EER)*Bin Hours
Cost of Electricity ($/ kwh) |  |  | 0.12
AC Unit Values | RTU # 1 | 0
Cooling Tonnage | 15 | 0
EER (Existing) | 9.368 | 8.1502
Heating Output (MBH) | 180 | 0
Heating Efficiency | 0.85 | 0.85
Fan HP | 1.5 | 1.5
Electric Heating | No | No
Energy & Cost Savings
| Cool Energy Savings (KWh) |  | Cost Savings ($)
RTU # 1 | 0 |  | 0
0 | 0 |  | 0
0 | 0 |  | 0
0 | 0 |  | 0
Totals | 0 |  | 0
Total Cooling Savings
| kWh | 0
| Dollars | 0
| Heating & Cooling Bin Data TMY3 |  | RTU # 1
Temp Mid-Point (T1) | Bin Hours | Equivalent Full Load Hours (%) at Each Bin | Existing Cooling kWh | Proposed Cooling kWh | Cooling kWh Saved
102.5 | 0 | 100% | 0 |  | 0
97.5 | 0 | 100% | 0 |  | 0
92.5 | 0 | 88.24% | 0 | 0 | 0
87.5 | 0 | 76.47% | 0 | 0 | 0
82.5 | 0 | 64.71% | 0 | 0 | 0
77.5 | 0 | 52.94% | 0 | 0 | 0
72.5 | 0 | 41.18% | 0 | 0 | 0
67.5 | 0 | 29.41% | 0 | 0 | 0
62.5 | 0 | 17.65% | 0 | 0 | 0
57.5 | 0 | 5.882%
52.5 | 0 | 3.333%
47.5 | 0 | 10%
42.5 | 0 | 16.67%
37.5 | 0 | 23.33%
32.5 | 0 | 30%
27.5 | 0 | 36.67%
22.5 | 0 | 43.33%
17.5 | 0 | 50%
12.5 | 0 | 56.67%
7.5 | 0 | 63.33%
2.5 | 0 | 70%
-2.5 | 0 | 76.67%
|  |  |  | Totals | 0
| Heating & Cooling Bin Data TMY3 |  | 0
Temp Mid-Point (T1) | Bin Hours | Equivalent Full Load Hours (%) at Each Bin | Existing Cooling kWh | Proposed Cooling kWh | Cooling kWh Saved
102.5 | 0 | 100% | 0 |  | 0
97.5 | 0 | 100% | 0 |  | 0
92.5 | 0 | 88.24% | 0 | 0 | 0
87.5 | 0 | 76.47% | 0 | 0 | 0
82.5 | 0 | 64.71% | 0 | 0 | 0
77.5 | 0 | 52.94% | 0 | 0 | 0
72.5 | 0 | 41.18% | 0 | 0 | 0
67.5 | 0 | 29.41% | 0 | 0 | 0
62.5 | 0 | 17.65% | 0 | 0 | 0
57.5 | 0 | 5.882%
52.5 | 0 | 3.333%
47.5 | 0 | 10%
42.5 | 0 | 16.67%
37.5 | 0 | 23.33%
32.5 | 0 | 30%
27.5 | 0 | 36.67%
22.5 | 0 | 43.33%
17.5 | 0 | 50%
12.5 | 0 | 56.67%
7.5 | 0 | 63.33%
2.5 | 0 | 70%
-2.5 | 0 | 76.67%
|  |  |  | Totals | 0

## ECM3.2 (hidden)
ECM- |  |  |  | #REF! | #REF!
Input Variables | [5 empty] | Equations & Variables
Cost of Electricity ($/ kwh) |  |  | 0.12 |  |  | Cooling Savings (kWh) |  | =Tons*(12/EER)*Bin Hours
Cost of Natural Gas ($/ Therm) |  |  | 1.3 |  |  | Heating Savings (kWh) |  | =Heat Capacity*Bin Hours*Load%
AHU Equipment Values | CH 1 | CH 2
Cooling Tonnage | 100 | 100
EER (Proposed) | 10.8 | 10.8
Exhaust Fans HP | #REF! | #REF!
Exhasut Fans Units | #REF! | #REF!
Electric Heat | No | No
Chiller Load Profile
Energy & Cost Savings | [6 empty] | OAT | EFLCH % (existing) | EFLHH % (proposed)
| Cooling Savings (KWh) |  |  | Cost Savings ($) |  |  | 58 | 100% | 100%
CH 1 | 28667.735 |  |  | 3440.1282 |  |  | 42 | 0% | 0%
CH 2 | 28667.735 |  |  | 3440.1282 |  |  | 58 | 100% | 100%
TOTAL | 57335.4701 |  |  | 6880.2564 |  |  | 45 | 0% | 0%
[7 empty] | Slope | 0.0625 | 0.076923
|  | Total Cooling Savings |  |  |  |  | Intercept | -2.625 | -3.4615
Cooling % |  | kWh | 57335.4701
Heating % |  | Dollars | 6880.2564
Implement Optimal Scheduling
| Heating & Cooling Bin Data TMY3 |  |  |  |  | CH 1
CH 1 | Temp Mid-Point | Bin Hours Existing | Equivalent Full Load Hours (%) at Each Bin | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 3 | 100% | 100% |  | 333.3333 | 333.3333 |  |  |  | 0
| 97.5 | 28 | 100% | 100% |  | 3111.1111 | 3111.1111 |  |  |  | 0
| 92.5 | 72 | 100% | 100% |  | 8000 | 8000 |  |  |  | 0
| 87.5 | 192 | 100% | 100% |  | 21333.3333 | 21333.3333 |  |  |  | 0
| 82.5 | 420 | 100% | 100% |  | 46666.6667 | 46666.6667 |  |  |  | 0
| 77.5 | 649 | 100% | 100% |  | 72111.1111 | 72111.1111 |  |  |  | 0
| 72.5 | 819 | 100% | 100% |  | 91000 | 91000 |  |  |  | 0
| 67.5 | 873 | 100% | 100% |  | 97000 | 97000 |  |  |  | 0
| 62.5 | 782 | 100% | 100% |  | 86888.8889 | 86888.8889 |  |  |  | 0
| 57.5 | 768 | 96.88% | 96.15% |  | 82666.6667 | 82051.2821 |  |  |  | 615.3846
| 52.5 | 795 | 65.62% | 57.69% |  | 57968.75 | 50961.5385 |  |  |  | 7007.2115
| 47.5 | 551 | 34.38% |  |  | 21045.1389 |  |  |  |  | 21045.1389
| 42.5 | 858
| 37.5 | 651
| 32.5 | 476
| 27.5 | 283
| 22.5 | 277
| 17.5 | 178
| 12.5 | 71
| 7.5 | 9
| 2.5 | 4 | -246.9%
| -2.5 | 1 | -278.1%
8760
[9 empty] | Totals | 0 | 28667.735
| Heating & Cooling Bin Data TMY3 |  |  |  |  | CH 2
CH 2 | Temp Mid-Point | Bin Hours Existing | Equivalent Full Load Hours (%) at Each Bin | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 3 | 100% | 100% |  | 333.3333 | 333.3333 |  |  |  | 0
| 97.5 | 28 | 100% | 100% |  | 3111.1111 | 3111.1111 |  |  |  | 0
| 92.5 | 72 | 100% | 100% |  | 8000 | 8000 |  |  |  | 0
| 87.5 | 192 | 100% | 100% |  | 21333.3333 | 21333.3333 |  |  |  | 0
| 82.5 | 420 | 100% | 100% |  | 46666.6667 | 46666.6667 |  |  |  | 0
| 77.5 | 649 | 100% | 100% |  | 72111.1111 | 72111.1111 |  |  |  | 0
| 72.5 | 819 | 100% | 100% |  | 91000 | 91000 |  |  |  | 0
| 67.5 | 873 | 100% | 100% |  | 97000 | 97000 |  |  |  | 0
| 62.5 | 782 | 100% | 100% |  | 86888.8889 | 86888.8889 |  |  |  | 0
| 57.5 | 768 | 96.88% | 96.15% |  | 82666.6667 | 82051.2821 |  |  |  | 615.3846
| 52.5 | 795 | 65.62% | 57.69% |  | 57968.75 | 50961.5385 |  |  |  | 7007.2115
| 47.5 | 551 | 34.38% |  |  | 21045.1389 |  |  |  |  | 21045.1389
| 42.5 | 858
| 37.5 | 651
| 32.5 | 476
| 27.5 | 283
| 22.5 | 277
| 17.5 | 178
| 12.5 | 71
| 7.5 | 9
| 2.5 | 4 | -246.9%
| -2.5 | 1 | -278.1%
8760
[9 empty] | Totals | 0 | 28667.735
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 3 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 28 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 72 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 192 | 192 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 420 | 420 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 649 | 624 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 819 | 716 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 873 | 747 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 782 | 688 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 768 | 657 | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | 795 | 686 | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | 551 | 483 | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | 858 | 726 | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | 651 | 540 | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | 476 | 395 | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | 283 | 239 | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | 277 | 231 | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | 178 | 153 | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 31 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 72 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 191 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 415 | 192 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 570 | 420 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 602 | 624 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 628 | 716 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 556 | 747 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 562 | 688 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 0 | 657 | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | 0 | 686 | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | 0 | 483 | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | 604 | 726 | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | 389 | 540 | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | 604 | 395 | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | 443 | 239 | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | 338 | 231 | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | 188 | 153 | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 3 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 28 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 72 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 191 | 190 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 415 | 409 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 564 | 547 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 571 | 529 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 582 | 536 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 526 | 485 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 525 | 499 | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | 567 | 533 | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | 367 | 338 | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | 562 | 520 | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | 404 | 378 | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | 307 | 292 | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | 177 | 160 | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | 176 | 166 | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | 125 | 114 | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 3 | 3 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 28 | 28 | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 72 | 72 | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 192 | 192 | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 420 | 420 | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 649 | 624 | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 819 | 716 | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 873 | 747 | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 782 | 688 | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 768 | 657 | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | 795 | 686 | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | 551 | 483 | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | 858 | 726 | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | 651 | 540 | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | 476 | 395 | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | 283 | 239 | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | 277 | 231 | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | 178 | 153 | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | #REF! | #REF! | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | #REF! | #REF! | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | #REF! | #REF! | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | #REF! | #REF! | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | #REF! | #REF! | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | #REF! | #REF! | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | #REF! | #REF! | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | #REF! | #REF! | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | #REF! | #REF! | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | #REF! | #REF! | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | #REF! | #REF! | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | #REF! | #REF! | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | #REF! | #REF! | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | #REF! | #REF! | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | #REF! | #REF! | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | #REF! | #REF! | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | #REF! | #REF! | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | #REF! | #REF! | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | #REF! | #REF! | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | #REF! | #REF! | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | #REF! | #REF! | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | #REF! | #REF! | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | #REF! | #REF! | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | #REF! | #REF! | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | #REF! | #REF! | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | #REF! | #REF! | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | #REF! | #REF! | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | #REF! | #REF! | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | #REF! | #REF! | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | #REF! | #REF! | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | #REF! | #REF! | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | #REF! | #REF! | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | #REF! | #REF! | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | #REF! | #REF! | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | #REF! | #REF! | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | #REF! | #REF! | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | #REF! | #REF! | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | #REF! | #REF! | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | #REF! | #REF! | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | #REF! | #REF! | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | #REF! | #REF! | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | #REF! | #REF! | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | #REF! | #REF! | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | #REF! | #REF! | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | #REF! | #REF! | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | #REF! | #REF! | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | #REF! | #REF! | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | #REF! | #REF! | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | #REF! | #REF! | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | #REF! | #REF! | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | #REF! | #REF! | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | #REF! | #REF! | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | #REF! | #REF! | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | #REF! | #REF! | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | #REF! | #REF! | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | #REF! | #REF! | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | #REF! | #REF! | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | #REF! | #REF! | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | #REF! | #REF! | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | #REF! | #REF! | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | #REF! | #REF! | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | #REF! | #REF! | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | #REF! | #REF! | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | #REF! | #REF! | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | #REF! | #REF! | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | #REF! | #REF! | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | #REF! | #REF! | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | #REF! | #REF! | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | #REF! | #REF! | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | #REF! | #REF! | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | #REF! | #REF! | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | #REF! | #REF! | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | #REF! | #REF! | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | #REF! | #REF! | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | #REF! | #REF! | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | #REF! | #REF! | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | #REF! | #REF! | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | #REF! | #REF! | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | #REF! | #REF! | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | #REF! | #REF! | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | #REF! | #REF! | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | #REF! | #REF! | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | #REF! | #REF! | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | #REF! | #REF! | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | #REF! | #REF! | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | #REF! | #REF! | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | #REF! | #REF! | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | #REF! | #REF! | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | #REF! | #REF! | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | #REF! | #REF! | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
|  | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | #REF! | #REF! | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | #REF! | #REF! | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | #REF! | #REF! | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | #REF! | #REF! | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | #REF! | #REF! | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | #REF! | #REF! | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | #REF! | #REF! | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | #REF! | #REF! | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | #REF! | #REF! | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | #REF! | #REF! | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | #REF! | #REF! | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | #REF! | #REF! | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | #REF! | #REF! | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | #REF! | #REF! | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | #REF! | #REF! | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | #REF! | #REF! | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | #REF! | #REF! | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | #REF! | #REF! | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
|  | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | #REF! | #REF! | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | #REF! | #REF! | 89.47% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | #REF! | #REF! | 78.95% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | #REF! | #REF! | 68.42% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | #REF! | #REF! | 57.89% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | #REF! | #REF! | 47.37% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | #REF! | #REF! | 36.84% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | #REF! | #REF! | 26.32% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | #REF! | #REF! | 15.79% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | #REF! | #REF! | 5.263% |  |  |  | #REF! | #REF!
| 52.5 | #REF! | #REF! | 4.348% |  |  |  | #REF! | #REF!
| 47.5 | #REF! | #REF! | 13.04% |  |  |  | #REF! | #REF!
| 42.5 | #REF! | #REF! | 21.74% |  |  |  | #REF! | #REF!
| 37.5 | #REF! | #REF! | 30.43% |  |  |  | #REF! | #REF!
| 32.5 | #REF! | #REF! | 39.13% |  |  |  | #REF! | #REF!
| 27.5 | #REF! | #REF! | 47.83% |  |  |  | #REF! | #REF!
| 22.5 | #REF! | #REF! | 56.52% |  |  |  | #REF! | #REF!
| 17.5 | #REF! | #REF! | 65.22% |  |  |  | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
|  | #REF! | #REF!
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 4 | 4 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 94 | 94 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 217 | 217 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 379 | 379 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 405 | 405 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 305 | 305 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 332 | 332 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 389 | 389 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 62.5 | 321 | 321 | 100% |  | #DIV/0! |  |  |  |  | #DIV/0!
| 57.5 | 326 | 326 | 96.88%
| 52.5 | 238 | 238 | 65.62%
| 47.5 | 290 | 290 | 34.38%
| 42.5 | 291 | 291 | 0%
| 37.5 | 196 | 196 | 0%
| 32.5 | 100 | 100 | 0%
| 27.5 | 95 | 95 | 0%
| 22.5 | 27 | 27 | 0%
| 17.5 | 6 | 6 | 0%
| 12.5 | 0 | 0 | 0%
| 7.5 | 0 | 0 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 4015 | 4015
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 493 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 614 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 713 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 910 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 842 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 560 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 793 | 96.88%
| 52.5 | 594 | 594 | 65.62%
| 47.5 | 670 | 670 | 34.38%
| 42.5 | 904 | 904 | 0%
| 37.5 | 566 | 566 | 0%
| 32.5 | 274 | 274 | 0%
| 27.5 | 225 | 225 | 0%
| 22.5 | 174 | 174 | 0%
| 17.5 | 99 | 99 | 0%
| 12.5 | 29 | 29 | 0%
| 7.5 | 4 | 4 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 8760
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 493 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 576 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 583 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 666 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 643 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 446 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 602 | 96.88%
| 52.5 | 594 | 466 | 65.62%
| 47.5 | 670 | 512 | 34.38%
| 42.5 | 904 | 687 | 0%
| 37.5 | 566 | 404 | 0%
| 32.5 | 274 | 188 | 0%
| 27.5 | 225 | 173 | 0%
| 22.5 | 174 | 117 | 0%
| 17.5 | 99 | 62 | 0%
| 12.5 | 29 | 17 | 0%
| 7.5 | 4 | 4 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 6935
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 493 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 576 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 583 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 666 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 643 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 446 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 602 | 96.88%
| 52.5 | 594 | 466 | 65.62%
| 47.5 | 670 | 512 | 34.38%
| 42.5 | 904 | 687 | 0%
| 37.5 | 566 | 404 | 0%
| 32.5 | 274 | 188 | 0%
| 27.5 | 225 | 173 | 0%
| 22.5 | 174 | 117 | 0%
| 17.5 | 99 | 62 | 0%
| 12.5 | 29 | 17 | 0%
| 7.5 | 4 | 4 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 6935
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 489 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 531 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 488 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 535 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 525 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 367 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 502 | 96.88%
| 52.5 | 594 | 390 | 65.62%
| 47.5 | 670 | 417 | 34.38%
| 42.5 | 904 | 557 | 0%
| 37.5 | 566 | 309 | 0%
| 32.5 | 274 | 145 | 0%
| 27.5 | 225 | 138 | 0%
| 22.5 | 174 | 90 | 0%
| 17.5 | 99 | 47 | 0%
| 12.5 | 29 | 11 | 0%
| 7.5 | 4 | 3 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 5840
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 493 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 576 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 583 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 666 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 643 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 446 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 602 | 96.88%
| 52.5 | 594 | 466 | 65.62%
| 47.5 | 670 | 512 | 34.38%
| 42.5 | 904 | 687 | 0%
| 37.5 | 566 | 404 | 0%
| 32.5 | 274 | 188 | 0%
| 27.5 | 225 | 173 | 0%
| 22.5 | 174 | 117 | 0%
| 17.5 | 99 | 62 | 0%
| 12.5 | 29 | 17 | 0%
| 7.5 | 4 | 4 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 6935
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 489 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 531 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 488 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 535 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 525 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 367 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 502 | 96.88%
| 52.5 | 594 | 390 | 65.62%
| 47.5 | 670 | 417 | 34.38%
| 42.5 | 904 | 557 | 0%
| 37.5 | 566 | 309 | 0%
| 32.5 | 274 | 145 | 0%
| 27.5 | 225 | 138 | 0%
| 22.5 | 174 | 90 | 0%
| 17.5 | 99 | 47 | 0%
| 12.5 | 29 | 11 | 0%
| 7.5 | 4 | 3 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 5840
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 489 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 531 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 488 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 535 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 525 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 367 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 502 | 96.88%
| 52.5 | 594 | 390 | 65.62%
| 47.5 | 670 | 417 | 34.38%
| 42.5 | 904 | 557 | 0%
| 37.5 | 566 | 309 | 0%
| 32.5 | 274 | 145 | 0%
| 27.5 | 225 | 138 | 0%
| 22.5 | 174 | 90 | 0%
| 17.5 | 99 | 47 | 0%
| 12.5 | 29 | 11 | 0%
| 7.5 | 4 | 3 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 5840
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 489 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 531 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 488 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 535 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 525 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 367 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 502 | 96.88%
| 52.5 | 594 | 390 | 65.62%
| 47.5 | 670 | 417 | 34.38%
| 42.5 | 904 | 557 | 0%
| 37.5 | 566 | 309 | 0%
| 32.5 | 274 | 145 | 0%
| 27.5 | 225 | 138 | 0%
| 22.5 | 174 | 90 | 0%
| 17.5 | 99 | 47 | 0%
| 12.5 | 29 | 11 | 0%
| 7.5 | 4 | 3 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 5840
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 493 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 614 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 713 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 910 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 842 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 560 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 793 | 96.88%
| 52.5 | 594 | 594 | 65.62%
| 47.5 | 670 | 670 | 34.38%
| 42.5 | 904 | 904 | 0%
| 37.5 | 566 | 566 | 0%
| 32.5 | 274 | 274 | 0%
| 27.5 | 225 | 225 | 0%
| 22.5 | 174 | 174 | 0%
| 17.5 | 99 | 99 | 0%
| 12.5 | 29 | 29 | 0%
| 7.5 | 4 | 4 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 8760
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 493 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 614 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 713 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 910 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 842 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 560 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 793 | 96.88%
| 52.5 | 594 | 594 | 65.62%
| 47.5 | 670 | 670 | 34.38%
| 42.5 | 904 | 904 | 0%
| 37.5 | 566 | 566 | 0%
| 32.5 | 274 | 274 | 0%
| 27.5 | 225 | 225 | 0%
| 22.5 | 174 | 174 | 0%
| 17.5 | 99 | 99 | 0%
| 12.5 | 29 | 29 | 0%
| 7.5 | 4 | 4 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 8760
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 493 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 614 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 713 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 910 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 842 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 560 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 793 | 96.88%
| 52.5 | 594 | 594 | 65.62%
| 47.5 | 670 | 670 | 34.38%
| 42.5 | 904 | 904 | 0%
| 37.5 | 566 | 566 | 0%
| 32.5 | 274 | 274 | 0%
| 27.5 | 225 | 225 | 0%
| 22.5 | 174 | 174 | 0%
| 17.5 | 99 | 99 | 0%
| 12.5 | 29 | 29 | 0%
| 7.5 | 4 | 4 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 8760
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | #REF!
#REF! | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 469 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 459 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 384 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 406 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 415 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 293 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 413 | 96.88%
| 52.5 | 594 | 312 | 65.62%
| 47.5 | 670 | 327 | 34.38%
| 42.5 | 904 | 427 | 0%
| 37.5 | 566 | 219 | 0%
| 32.5 | 274 | 114 | 0%
| 27.5 | 225 | 107 | 0%
| 22.5 | 174 | 63 | 0%
| 17.5 | 99 | 31 | 0%
| 12.5 | 29 | 8 | 0%
| 7.5 | 4 | 2 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 4745
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 489 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 531 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 488 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 535 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 525 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 367 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 502 | 96.88%
| 52.5 | 594 | 390 | 65.62%
| 47.5 | 670 | 417 | 34.38%
| 42.5 | 904 | 557 | 0%
| 37.5 | 566 | 309 | 0%
| 32.5 | 274 | 145 | 0%
| 27.5 | 225 | 138 | 0%
| 22.5 | 174 | 90 | 0%
| 17.5 | 99 | 47 | 0%
| 12.5 | 29 | 11 | 0%
| 7.5 | 4 | 3 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 5840
[9 empty] | Totals | 0 | #DIV/0!
| Heating & Cooling Bin Data TMY3 |  |  |  |  | 0
0 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin |  | Existing Cooling kWh | Proposed Cooling kWh | Existing Heating (kWh) | Proposed Heating (kWh) | Heating kWh Saved | Cooling kWh Saved
| 102.5 | 18 | 18 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 97.5 | 63 | 63 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 92.5 | 215 | 215 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 87.5 | 493 | 469 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 82.5 | 614 | 463 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 77.5 | 713 | 404 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 72.5 | 910 | 454 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 67.5 | 842 | 457 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 62.5 | 560 | 320 | 100% |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0!
| 57.5 | 793 | 444 | 96.88%
| 52.5 | 594 | 339 | 65.62%
| 47.5 | 670 | 355 | 34.38%
| 42.5 | 904 | 479 | 0%
| 37.5 | 566 | 249 | 0%
| 32.5 | 274 | 127 | 0%
| 27.5 | 225 | 123 | 0%
| 22.5 | 174 | 76 | 0%
| 17.5 | 99 | 41 | 0%
| 12.5 | 29 | 11 | 0%
| 7.5 | 4 | 3 | 0%
| 2.5 | 0 | 0 | -246.9%
| -2.5 | 0 | 0 | -278.1%
|  | 8760 | 5110
[9 empty] | Totals | 0 | #DIV/0!

## ECM2
ECM- |  |  |  | 2 | AHU temperature scale adjustment
Input Variables |  |  |  |  | Equations & Variables
System Efficiency (Heating) |  | See Below |  |  | Energy Equation (Cooling kWh) |  | =Tons*(12/EER)*Bin Hours
System Efficiency (Cooling EER) |  | See Below |  |  | Energy Equation (Heating) |  | =(1.08*CFM*DT*Bin Hours)/3412.14
Cost of Electricity ($/ kwh) |  | 0.12 |  |  | Fan Savings (kWh) |  | =((HP*Mtr Load %*.746)/Mtr Eff * VFD eff) * VFD Speed^fan law exponent
Cost of Electricity ($/ Therm) |  | 1.3
| AHU #1 | AHU #2 | AHU #3 | AHU #4 | AHU #5 | AHU #6 | AHU #7 | RTU # 1
Cooling Tons | 39.1 | 61.6 | 66.5 | 17.6 | 2.6 | 7.5 | 3.4 | 15
Heating MBH | 469.2 | 739.2 | 798 | 211.2 | 31.2 | 90 | 40.8 | 180 | 0
Heating eff % | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
Cooling EER | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 10
Cooling Eff (kw/Ton) | 1.0619 | 1.0619 | 1.0619 | 1.0619 | 1.0619 | 1.0619 | 1.0619 | 1.2
Supply Fan Max CFM | 15640 | 24640 | 26600 | 7040 | 1040 | 3000 | 1360 | 6000
Supply Fan Min CFM | 3910 | 6160 | 6650 | 1760 | 260 | 750 | 340 | 1500
Energy & Cost Savings | bar: AHU #1 to 1.3 AHU #5
| Heating Energy Savings (Therms) |  |  | Cost Savings ($)
AHU #1 | AHU #1: 653.3869; 1.3 AHU #4: 849.403
AHU #2 | AHU #1: 19.873; 1.3 AHU #4: 25.8349
AHU #3 | AHU #1: 185.2837; 1.3 AHU #4: 240.8688
AHU #4 | AHU #1: 138.8332; 1.3 AHU #4: 180.4831
AHU #5 | AHU #1: 15.836; 1.3 AHU #4: 20.5867
AHU #6 | AHU #1: 1.7663; 1.3 AHU #4: 2.2962
AHU #7 | AHU #1: 0.041134; 1.3 AHU #4: 0.053474
RTU # 1 | AHU #1: 128.8539; 1.3 AHU #4: 167.51
Totals | AHU #1: 1143.874; 1.3 AHU #4: 1487.0362
Total Gas Savings (Heating)
|  | kHw | 1143.874
|  | Dollars | 1487.0362
RTU Load Profile
| OAT | EFLCH % | EFLHH %
| 102.5 | 100%
| 55 | 0%
| 55 |  | 0%
| -2.5 |  | 100%
| Slope | 0.021053 | -0.017391
| Intercept | -1.1579 | 0.95652
AHU #1
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
AHU #1 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 3 |  | 100%
| 97.5 | 28 |  | 89.47%
| 92.5 | 72 |  | 78.95%
| 87.5 | 192 |  | 68.42%
| 82.5 | 420 |  | 57.89%
| 77.5 | 649 |  | 47.37%
| 72.5 | 819 |  | 36.84%
| 67.5 | 873 |  | 26.32%
| 62.5 | 782 |  | 15.79%
| 57.5 | 768 |  | 5.263%
| 52.5 | 795 | 20.4 | 4.348% | 7447.619 | 70 | 75 |  |  | 5 | 13.9011
| 47.5 | 551 | 61.2 | 13.04% | 8192.381 | 70 | 75 |  |  | 5 | 31.7943
| 42.5 | 858 | 102 | 21.74% | 8937.1429 | 70 | 75 |  |  | 5 | 90.0165
| 37.5 | 651 | 142.8 | 30.43% | 9681.9048 | 70 | 75 |  |  | 5 | 103.5871
| 32.5 | 476 | 183.6 | 39.13% | 10426.6667 | 70 | 75 |  |  | 5 | 104.8723
| 27.5 | 283 | 224.4 | 47.83% | 11171.4286 | 70 | 75 |  |  | 5 | 81.6495
| 22.5 | 277 | 265.2 | 56.52% | 11916.1905 | 70 | 75 |  |  | 5 | 100.7457
| 17.5 | 178 | 306 | 65.22% | 12660.9524 | 70 | 75 |  |  | 5 | 79.3677
| 12.5 | 71 | 346.8 | 73.91% | 13405.7143 | 70 | 75 |  |  | 5 | 37.9895
| 7.5 | 9 | 387.6 | 82.61% | 14150.4762 | 70 | 75 |  |  | 5 | 5.6811
| 2.5 | 4 | 428.4 | 91.3% | 14895.2381 | 70 | 75 |  |  | 5 | 2.9376
| -2.5 | 1 | 469.2 | 100% | 15640 | 70 | 75 |  |  | 5 | 0.84456
653.3869
AHU #2
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
AHU #2 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 2 |  | 100% |  | 65 | 70
| 97.5 | 2 |  | 89.47% |  | 65 | 70
| 92.5 | 6 |  | 78.95% |  | 65 | 70
| 87.5 | 20 |  | 68.42% |  | 65 | 70
| 82.5 | 37 |  | 57.89% |  | 65 | 70
| 77.5 | 20 |  | 47.37% |  | 65 | 70
| 72.5 | 23 |  | 36.84% |  | 65 | 70
| 67.5 | 14 |  | 26.32% |  | 65 | 70
| 62.5 | 15 |  | 15.79% |  | 65 | 70
| 57.5 | 30 |  | 5.263% |  | 65 | 70
| 52.5 | 21 | 32.1391 | 4.348% | 11733.3333 | 70 | 75 |  |  | 5 | 0.5785
| 47.5 | 24 | 96.4174 | 13.04% | 12906.6667 | 70 | 75 |  |  | 5 | 2.1818
| 42.5 | 11 | 160.6957 | 21.74% | 14080 | 70 | 75 |  |  | 5 | 1.8182
| 37.5 | 11 | 224.9739 | 30.43% | 15253.3333 | 70 | 75 |  |  | 5 | 2.7575
| 32.5 | 3 | 289.2522 | 39.13% | 16426.6667 | 70 | 75 |  |  | 5 | 1.0413
| 27.5 | 10 | 353.5304 | 47.83% | 17600 | 70 | 75 |  |  | 5 | 4.5454
| 22.5 | 6 | 417.8087 | 56.52% | 18773.3333 | 70 | 75 |  |  | 5 | 3.438
| 17.5 | 5 | 482.087 | 65.22% | 19946.6667 | 70 | 75 |  |  | 5 | 3.5123
| 12.5 | 0 | 546.3652 | 73.91% | 21120 | 70 | 75 |  |  | 5 | 0
| 7.5 | 0 | 610.6435 | 82.61% | 22293.3333 | 70 | 75 |  |  | 5 | 0
| 2.5 | 0 | 674.9217 | 91.3% | 23466.6667 | 70 | 75 |  |  | 5 | 0
| -2.5 | 0 | 739.2 | 100% | 24640 | 70 | 75 |  |  | 5 | 0
19.873
AHU #3
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
AHU #3 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 0 |  | 100% |  | 65 | 70
| 97.5 | 0 |  | 89.47% |  | 65 | 70
| 92.5 | 2 |  | 78.95% |  | 65 | 70
| 87.5 | 11 |  | 68.42% |  | 65 | 70
| 82.5 | 77 |  | 57.89% |  | 65 | 70
| 77.5 | 187 |  | 47.37% |  | 65 | 70
| 72.5 | 211 |  | 36.84% |  | 65 | 70
| 67.5 | 203 |  | 26.32% |  | 65 | 70
| 62.5 | 158 |  | 15.79% |  | 65 | 70
| 57.5 | 153 |  | 5.263% |  | 65 | 70
| 52.5 | 145 | 34.6957 | 4.348% | 12666.6667 | 70 | 75 |  |  | 5 | 4.3122
| 47.5 | 206 | 104.087 | 13.04% | 13933.3333 | 70 | 75 |  |  | 5 | 20.2167
| 42.5 | 162 | 173.4783 | 21.74% | 15200 | 70 | 75 |  |  | 5 | 28.9064
| 37.5 | 103 | 242.8696 | 30.43% | 16466.6667 | 70 | 75 |  |  | 5 | 27.8745
| 32.5 | 79 | 312.2609 | 39.13% | 17733.3333 | 70 | 75 |  |  | 5 | 29.6023
| 27.5 | 65 | 381.6522 | 47.83% | 19000 | 70 | 75 |  |  | 5 | 31.8952
| 22.5 | 39 | 451.0435 | 56.52% | 20266.6667 | 70 | 75 |  |  | 5 | 24.1244
| 17.5 | 23 | 520.4348 | 65.22% | 21533.3333 | 70 | 75 |  |  | 5 | 17.442
| 12.5 | 1 | 589.8261 | 73.91% | 22800 | 70 | 75 |  |  | 5 | 0.91002
| 7.5 | 0 | 659.2174 | 82.61% | 24066.6667 | 70 | 75 |  |  | 5 | 0
| 2.5 | 0 | 728.6087 | 91.3% | 25333.3333 | 70 | 75 |  |  | 5 | 0
| -2.5 | 0 | 798 | 100% | 26600 | 70 | 75 |  |  | 5 | 0
185.2837
AHU #4
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
AHU #4 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 5 |  | 100% |  | 65 | 70
| 97.5 | 40 |  | 89.47% |  | 65 | 70
| 92.5 | 229 |  | 78.95% |  | 65 | 70
| 87.5 | 435 |  | 68.42% |  | 65 | 70
| 82.5 | 713 |  | 57.89% |  | 65 | 70
| 77.5 | 775 |  | 47.37% |  | 65 | 70
| 72.5 | 1091 |  | 36.84% |  | 65 | 70
| 67.5 | 1039 |  | 26.32% |  | 65 | 70
| 62.5 | 894 |  | 15.79% |  | 65 | 70
| 57.5 | 759 |  | 5.263% |  | 65 | 70
| 52.5 | 640 | 9.1826 | 4.348% | 3352.381 | 70 | 75 |  |  | 5 | 5.0373
| 47.5 | 671 | 27.5478 | 13.04% | 3687.619 | 70 | 75 |  |  | 5 | 17.4283
| 42.5 | 673 | 45.913 | 21.74% | 4022.8571 | 70 | 75 |  |  | 5 | 31.7823
| 37.5 | 287 | 64.2783 | 30.43% | 4358.0952 | 70 | 75 |  |  | 5 | 20.5562
| 32.5 | 196 | 82.6435 | 39.13% | 4693.3333 | 70 | 75 |  |  | 5 | 19.4377
| 27.5 | 214 | 101.0087 | 47.83% | 5028.5714 | 70 | 75 |  |  | 5 | 27.7918
| 22.5 | 83 | 119.3739 | 56.52% | 5363.8095 | 70 | 75 |  |  | 5 | 13.5882
| 17.5 | 10 | 137.7391 | 65.22% | 5699.0476 | 70 | 75 |  |  | 5 | 2.0071
| 12.5 | 5 | 156.1043 | 73.91% | 6034.2857 | 70 | 75 |  |  | 5 | 1.2042
| 7.5 | 1 | 174.4696 | 82.61% | 6369.5238 | 70 | 75 |  |  | 5 | 0.28414
| 2.5 | 0 | 192.8348 | 91.3% | 6704.7619 | 70 | 75 |  |  | 5 | 0
| -2.5 | 0 | 211.2 | 100% | 7040 | 70 | 75 |  |  | 5 | 0
138.8332
AHU #5
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
AHU #5 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 3 |  | 100% |  | 65 | 70
| 97.5 | 26 |  | 89.47% |  | 65 | 70
| 92.5 | 67 |  | 78.95% |  | 65 | 70
| 87.5 | 172 |  | 68.42% |  | 65 | 70
| 82.5 | 356 |  | 57.89% |  | 65 | 70
| 77.5 | 440 |  | 47.37% |  | 65 | 70
| 72.5 | 344 |  | 36.84% |  | 65 | 70
| 67.5 | 325 |  | 26.32% |  | 65 | 70
| 62.5 | 334 |  | 15.79% |  | 65 | 70
| 57.5 | 346 |  | 5.263% |  | 65 | 70
| 52.5 | 337 | 1.3565 | 4.348% | 495.2381 | 70 | 75 |  |  | 5 | 0.39184
| 47.5 | 229 | 4.0696 | 13.04% | 544.7619 | 70 | 75 |  |  | 5 | 0.87868
| 42.5 | 328 | 6.7826 | 21.74% | 594.2857 | 70 | 75 |  |  | 5 | 2.2883
| 37.5 | 227 | 9.4957 | 30.43% | 643.8095 | 70 | 75 |  |  | 5 | 2.4019
| 32.5 | 193 | 12.2087 | 39.13% | 693.3333 | 70 | 75 |  |  | 5 | 2.8275
| 27.5 | 93 | 14.9217 | 47.83% | 742.8571 | 70 | 75 |  |  | 5 | 1.7842
| 22.5 | 108 | 17.6348 | 56.52% | 792.381 | 70 | 75 |  |  | 5 | 2.612
| 17.5 | 65 | 20.3478 | 65.22% | 841.9048 | 70 | 75 |  |  | 5 | 1.9272
| 12.5 | 18 | 23.0609 | 73.91% | 891.4286 | 70 | 75 |  |  | 5 | 0.64043
| 7.5 | 2 | 25.7739 | 82.61% | 940.9524 | 70 | 75 |  |  | 5 | 0.083949
| 2.5 | 1 | 28.487 | 91.3% | 990.4762 | 70 | 75 |  |  | 5 | 0.048835
| -2.5 | 1 | 31.2 | 100% | 1040 | 70 | 75 |  |  | 5 | 0.05616
15.836
AHU #6
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
AHU #6 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 3 |  | 100% |  | 65 | 70
| 97.5 | 5 |  | 89.47% |  | 65 | 70
| 92.5 | 20 |  | 78.95% |  | 65 | 70
| 87.5 | 39 |  | 68.42% |  | 65 | 70
| 82.5 | 48 |  | 57.89% |  | 65 | 70
| 77.5 | 41 |  | 47.37% |  | 65 | 70
| 72.5 | 30 |  | 36.84% |  | 65 | 70
| 67.5 | 21 |  | 26.32% |  | 65 | 70
| 62.5 | 39 |  | 15.79% |  | 65 | 70
| 57.5 | 42 |  | 5.263% |  | 65 | 70
| 52.5 | 23 | 3.913 | 4.348% | 1428.5714 | 70 | 75 |  |  | 5 | 0.0061927
| 47.5 | 37 | 11.7391 | 13.04% | 1571.4286 | 70 | 75 |  |  | 5 | 0.08966
| 42.5 | 18 | 19.5652 | 21.74% | 1714.2857 | 70 | 75 |  |  | 5 | 0.12116
| 37.5 | 14 | 27.3913 | 30.43% | 1857.1429 | 70 | 75 |  |  | 5 | 0.1847
| 32.5 | 6 | 35.2174 | 39.13% | 2000 | 70 | 75 |  |  | 5 | 0.13085
| 27.5 | 16 | 43.0435 | 47.83% | 2142.8571 | 70 | 75 |  |  | 5 | 0.52127
| 22.5 | 9 | 50.8696 | 56.52% | 2285.7143 | 70 | 75 |  |  | 5 | 0.40953
| 17.5 | 5 | 58.6957 | 65.22% | 2428.5714 | 70 | 75 |  |  | 5 | 0.3029
| 12.5 | 0 | 66.5217 | 73.91% | 2571.4286 | 70 | 75 |  |  | 5 | 0
| 7.5 | 0 | 74.3478 | 82.61% | 2714.2857 | 70 | 75 |  |  | 5 | 0
| 2.5 | 0 | 82.1739 | 91.3% | 2857.1429 | 70 | 75 |  |  | 5 | 0
| -2.5 | 0 | 90 | 100% | 3000 | 70 | 75 |  |  | 5 | 0
1.7663
AHU #7
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
AHU #7 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 3 |  | 100% |  | 65 | 70
| 97.5 | 26 |  | 89.47% |  | 65 | 70
| 92.5 | 67 |  | 78.95% |  | 65 | 70
| 87.5 | 172 |  | 68.42% |  | 65 | 70
| 82.5 | 356 |  | 57.89% |  | 65 | 70
| 77.5 | 440 |  | 47.37% |  | 65 | 70
| 72.5 | 344 |  | 36.84% |  | 65 | 70
| 67.5 | 325 |  | 26.32% |  | 65 | 70
| 62.5 | 334 |  | 15.79% |  | 65 | 70
| 57.5 | 346 |  | 5.263% |  | 65 | 70
| 52.5 | 337 | 1.7739 | 4.348% | 647.619 | 70 | 75 |  |  | 5 | 0.041134
| 47.5 | 229 | 5.3217 | 13.04% | 712.381 | 70 | 75 |  |  | 5 | 0.25156
| 42.5 | 328 | 8.8696 | 21.74% | 777.1429 | 70 | 75 |  |  | 5 | 1.0009
| 37.5 | 227 | 12.4174 | 30.43% | 841.9048 | 70 | 75 |  |  | 5 | 1.3577
| 32.5 | 193 | 15.9652 | 39.13% | 906.6667 | 70 | 75 |  |  | 5 | 1.9082
| 27.5 | 93 | 19.513 | 47.83% | 971.4286 | 70 | 75 |  |  | 5 | 1.3735
| 22.5 | 108 | 23.0609 | 56.52% | 1036.1905 | 70 | 75 |  |  | 5 | 2.2278
| 17.5 | 65 | 26.6087 | 65.22% | 1100.9524 | 70 | 75 |  |  | 5 | 1.7851
| 12.5 | 18 | 30.1565 | 73.91% | 1165.7143 | 70 | 75 |  |  | 5 | 0.63495
| 7.5 | 2 | 33.7043 | 82.61% | 1230.4762 | 70 | 75 |  |  | 5 | 0.088127
| 2.5 | 1 | 37.2522 | 91.3% | 1295.2381 | 70 | 75 |  |  | 5 | 0.053828
| -2.5 | 1 | 40.8 | 100% | 1360 | 70 | 75 |  |  | 5 | 0.064569
0.041134
RTU # 1
| AHU #1: Heating & Cooling Bin Data TMY3; 1.3 AHU #6: System Temperatures |  | Heating Savings
RTU # 1 | Temp Mid-Point | Bin Hours Proposed | Cooling Load (MBH) | Equivalent Full Load Hours (%) at Each Bin | Supply Fan CFM | Supply Air Temperature (Existing) | Supply Air Temperature (Proposed) |  |  | Htg dT Proposed (deg F) | Heating Therms Saved
| 102.5 | 3 |  | 100% |  | 65 | 70
| 97.5 | 28 |  | 89.47% |  | 65 | 70
| 92.5 | 72 |  | 78.95% |  | 65 | 70
| 87.5 | 192 |  | 68.42% |  | 65 | 70
| 82.5 | 420 |  | 57.89% |  | 65 | 70
| 77.5 | 649 |  | 47.37% |  | 65 | 70
| 72.5 | 819 |  | 36.84% |  | 65 | 70
| 67.5 | 873 |  | 26.32% |  | 65 | 70
| 62.5 | 782 |  | 15.79% |  | 65 | 70
| 57.5 | 768 |  | 5.263% |  | 65 | 70
| 52.5 | 795 | 7.8261 | 4.348% | 2857.1429 | 70 | 75 |  |  | 5 | 0.42811
| 47.5 | 551 | 23.4783 | 13.04% | 3142.8571 | 70 | 75 |  |  | 5 | 2.6704
| 42.5 | 858 | 39.1304 | 21.74% | 3428.5714 | 70 | 75 |  |  | 5 | 11.5508
| 37.5 | 651 | 54.7826 | 30.43% | 3714.2857 | 70 | 75 |  |  | 5 | 17.1775
| 32.5 | 476 | 70.4348 | 39.13% | 4000 | 70 | 75 |  |  | 5 | 20.7623
| 27.5 | 283 | 86.087 | 47.83% | 4285.7143 | 70 | 75 |  |  | 5 | 18.4398
| 22.5 | 277 | 101.7391 | 56.52% | 4571.4286 | 70 | 75 |  |  | 5 | 25.2087
| 17.5 | 178 | 117.3913 | 65.22% | 4857.1429 | 70 | 75 |  |  | 5 | 21.5668
| 12.5 | 71 | 133.0435 | 73.91% | 5142.8571 | 70 | 75 |  |  | 5 | 11.0494
| 7.5 | 9 | 148.6957 | 82.61% | 5428.5714 | 70 | 75 |  |  | 5 | 1.7496
| 2.5 | 4 | 164.3478 | 91.3% | 5714.2857 | 70 | 75 |  |  | 5 | 0.94991
| -2.5 | 1 | 180 | 100% | 6000 | 70 | 75 |  |  | 5 | 0.28487
128.8539

## ECM5.2 (hidden)
ECM- |  |  |  | #REF! | #REF!
Input Variables | [5 empty] | Equations & Variables
Cost of Electricity ($/ kwh) |  |  | 0.12 |  |  | Cooling Savings (kWh) | =Tons*(12/EER)*Bin Hours
Cost of Natural Gas ($/ Therm) |  |  | 1.3 |  |  | Heating Savings (kWh) | =Heat Capacity*Bin Hours*Load%
AHU Equipment Values | Walk-in 1
Cooling Tonnage | 6.5
EER (Proposed) | 1.2
Heating Capacity (MBH) | 78
Heating Efficiency | 0.85
Supply Fan HP | 0.049713
Supply Fan Units | 1
Exhaust Fans HP | #REF!
Exhasut Fans Units | #REF!
Electric Heat | No
Number of VAV | 15
Energy & Cost Savings
| Supply Fan Energy Savings (kWh) |  | Cost Savings ($)
Walk-in 1 | 3401.5065 |  | 408.1808
TOTAL | 3401.5065 |  | 408.1808
Total Electrical Savings
Cooling % |  | kWh | 3401.5065
Heating % |  | Dollars | 408.1808
Implement Optimal Scheduling
Heating & Cooling Bin Data TMY3
Walk-in 1 | Temp Mid-Point | Bin Hours Existing | Bin Hours Proposed | Equivalent Full Load Hours (%) at Each Bin | Total Reduction in Bin Hours | Existing Fan kWh
| 102.5 | 3 | 3 | 100% | 0 | 0
| 97.5 | 28 | 26 | 100% | 2 | 0.060241
| 92.5 | 72 | 67 | 88.24% | 12.8824 | 0.38802
| 87.5 | 192 | 172 | 76.47% | 60.4706 | 1.8214
| 82.5 | 420 | 354 | 64.71% | 190.9412 | 5.7512
| 77.5 | 649 | 419 | 52.94% | 427.1765 | 12.8667
| 72.5 | 819 | 303 | 41.18% | 694.2353 | 20.9106
| 67.5 | 873 | 292 | 29.41% | 787.1176 | 23.7083
| 62.5 | 782 | 301 | 17.65% | 728.8824 | 21.9542
| 57.5 | 768 | 313 | 5.882% | 749.5882 | 22.5779
| 52.5 | 795 | 300 | 3.333% | 785 | 23.6445
| 47.5 | 551 | 210 | 10% | 530 | 15.9638
| 42.5 | 858 | 290 | 16.67% | 809.6667 | 24.3875
| 37.5 | 651 | 195 | 23.33% | 605.5 | 18.2379
| 32.5 | 476 | 164 | 30% | 426.8 | 12.8554
| 27.5 | 283 | 80 | 36.67% | 253.6667 | 7.6405
| 22.5 | 277 | 95 | 43.33% | 235.8333 | 7.1034
| 17.5 | 178 | 52 | 50% | 152 | 4.5783
| 12.5 | 71 | 13 | 56.67% | 63.6333 | 1.9167
| 7.5 | 9 | 0 | 63.33% | 9 | 0.27108
| 2.5 | 4 | 1 | 70% | 3.3 | 0.099397
| -2.5 | 1 | 0 | 76.67% | 1 | 0.03012
|  | 8760 | 3650
[5 empty] | TOTALS | 226.7671

## ECM6 (3) (hidden)
ECM- |  |  |  | 6 | Adjust AHU Unoccupied Heating Set Points
Input Variables |  |  |  |  | Equations & Variables
System Efficiency (Heating) |  | See Below |  |  | Energy Equation (kWh) |  | =kW*FLH Bin Hours
System Efficiency (Cooling EER) |  | See Below
Cost of Electricity ($/ kwh) |  | 0.12
Equipment Values from O&M Manual | AHU 1 | AHU 2 | AHU 3 | AHU 4 | AHU 5 | AHU 6 | AHU 7 | AHU 8 | AHU 9 | AHU 10 | AHU 11 | AHU 12 | AHU 13 | AHU 14 | AHU 15
Tonnage | 69.5833 | 36.8333 | 13.4167 | 13.6667 | 14 | 4.1667 | 4.1667 | 9 | 6.25 | 2.3917 | 6.8333 | 67.3333 | 17.9167 | 7.8417 | 33.6667
kW RTU | 244.7141 | 129.5373 | 47.1844 | 48.0636 | 49.2359 | 14.6535 | 14.6535 | 31.6517 | 21.9803 | 8.4111 | 24.0318 | 236.8012 | 63.0102 | 27.578 | 118.4006
Motor HP | 25 | 15 | 2 | 2 | 2 | 0.5 | 0.5 | 1 | 1 | 0.75 | 1 | 7.5 | 5 | 7.5 | 2
kw RTU Fan motor | 18.6425 | 11.1855 | 1.4914 | 1.4914 | 1.4914 | 0.37285 | 0.37285 | 0.7457 | 0.7457 | 0.55927 | 0.7457 | 5.5927 | 3.7285 | 5.5927 | 1.4914
Total Number of Fan motor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total kW | 18.6425 | 11.1855 | 1.4914 | 1.4914 | 1.4914 | 0.37285 | 0.37285 | 0.7457 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy & Cost Savings
| Energy Savings (KWh) |  |  | Cost Savings ($)
AHU 1 | AHU 1: 753.1246; AHU 4: 90.3749
AHU 2 | AHU 1: 451.8747; AHU 4: 54.225
AHU 3 | AHU 1: 60.25; AHU 4: 7.23
AHU 4 | AHU 1: 60.25; AHU 4: 7.23
AHU 5 | AHU 1: 60.25; AHU 4: 7.23
AHU 6 | AHU 1: 15.0625; AHU 4: 1.8075
AHU 7 | AHU 1: 15.0625; AHU 4: 1.8075
AHU 8 | AHU 1: 30.125; AHU 4: 3.615
AHU 9 | AHU 1: 30.125; AHU 4: 3.615
AHU 10 | AHU 1: 30.125; AHU 4: 3.615
AHU 11 | AHU 1: 30.125; AHU 4: 3.615
AHU 12 | AHU 1: 121.8576; AHU 4: 14.6229
AHU 13 | AHU 1: 232.4564; AHU 4: 27.8948
AHU 14 | AHU 1: 91.6487; AHU 4: 10.9978
AHU 15 | AHU 1: 40.3983; AHU 4: 4.8478
Totals | AHU 1: 2022.7351; AHU 4: 242.7282
Total Electric Savings
| kWh | 2022.7351
| Dollars | 242.7282
Full Load Operating Hours Calculation | bar: AHU 1 to AHU 8
Heating & Cooling Bin Data TMY3
AHU 1 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0% | 0% | 0 | 0 | 0
| 67.5 | 126 | 0% | 0% | 0 | 0 | 0
| 62.5 | 94 | 0% | 0% | 0 | 0 | 0
| 57.5 | 111 | 4% | 0% | 4.44 | 0 | 4.44
| 52.5 | 109 | 12% | 4.348% | 13.08 | 4.7391 | 8.3409
| 47.5 | 68 | 20% | 13.04% | 13.6 | 8.8696 | 4.7304
| 42.5 | 132 | 28% | 21.74% | 36.96 | 28.6957 | 8.2643
| 37.5 | 111 | 36% | 30.43% | 39.96 | 33.7826 | 6.1774
| 32.5 | 81 | 44% | 39.13% | 35.64 | 31.6957 | 3.9443
| 27.5 | 44 | 52% | 47.83% | 22.88 | 21.0435 | 1.8365
| 22.5 | 46 | 60% | 56.52% | 27.6 | 26 | 1.6
| 17.5 | 25 | 68% | 65.22% | 17 | 16.3043 | 0.69565
| 12.5 | 14 | 76% | 73.91% | 10.64 | 10.3478 | 0.29217
| 7.5 | 4 | 84% | 82.61% | 3.36 | 3.3043 | 0.055652
| 2.5 | 3 | 92% | 91.3% | 2.76 | 2.7391 | 0.02087
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 40.3983
AHU 2 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0.6623% | 0% | 0.68212 | 0 | 0.68212
| 67.5 | 126 | 7.285% | 0% | 9.1788 | 0 | 9.1788
| 62.5 | 94 | 13.91% | 0% | 13.0728 | 0 | 13.0728
| 57.5 | 111 | 20.53% | 0% | 22.7881 | 0 | 22.7881
| 52.5 | 109 | 27.15% | 4.348% | 29.596 | 4.7391 | 24.8569
| 47.5 | 68 | 33.77% | 13.04% | 22.9669 | 8.8696 | 14.0973
| 42.5 | 132 | 40.4% | 21.74% | 53.3245 | 28.6957 | 24.6289
| 37.5 | 111 | 47.02% | 30.43% | 52.1921 | 33.7826 | 18.4094
| 32.5 | 81 | 53.64% | 39.13% | 43.4503 | 31.6957 | 11.7547
| 27.5 | 44 | 60.26% | 47.83% | 26.5166 | 21.0435 | 5.4731
| 22.5 | 46 | 66.89% | 56.52% | 30.7682 | 26 | 4.7682
| 17.5 | 25 | 73.51% | 65.22% | 18.3775 | 16.3043 | 2.0731
| 12.5 | 14 | 80.13% | 73.91% | 11.2185 | 10.3478 | 0.87072
| 7.5 | 4 | 86.75% | 82.61% | 3.4702 | 3.3043 | 0.16585
| 2.5 | 3 | 93.38% | 91.3% | 2.8013 | 2.7391 | 0.062194
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 152.2001
AHU 3 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 1 | 0% | 0% | 0 | 0 | 0
| 92.5 | 4 | 0% | 0% | 0 | 0 | 0
| 87.5 | 17 | 0% | 0% | 0 | 0 | 0
| 82.5 | 47 | 0% | 0% | 0 | 0 | 0
| 77.5 | 156 | 0% | 0% | 0 | 0 | 0
| 72.5 | 374 | 0% | 0% | 0 | 0 | 0
| 67.5 | 440 | 0% | 0% | 0 | 0 | 0
| 62.5 | 364 | 3.704% | 0% | 13.4815 | 0 | 13.4815
| 57.5 | 347 | 11.11% | 0% | 38.5556 | 0 | 38.5556
| 52.5 | 364 | 18.52% | 4.348% | 67.4074 | 15.8261 | 51.5813
| 47.5 | 268 | 25.93% | 13.04% | 69.4815 | 34.9565 | 34.525
| 42.5 | 392 | 33.33% | 21.74% | 130.6667 | 85.2174 | 45.4493
| 37.5 | 329 | 40.74% | 30.43% | 134.037 | 100.1304 | 33.9066
| 32.5 | 238 | 48.15% | 39.13% | 114.5926 | 93.1304 | 21.4622
| 27.5 | 152 | 55.56% | 47.83% | 84.4444 | 72.6957 | 11.7488
| 22.5 | 130 | 62.96% | 56.52% | 81.8519 | 73.4783 | 8.3736
| 17.5 | 86 | 70.37% | 65.22% | 60.5185 | 56.087 | 4.4316
| 12.5 | 32 | 77.78% | 73.91% | 24.8889 | 23.6522 | 1.2367
| 7.5 | 7 | 85.19% | 82.61% | 5.963 | 5.7826 | 0.18035
| 2.5 | 3 | 92.59% | 91.3% | 2.7778 | 2.7391 | 0.038647
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 3751 |  |  |  | Totals | 264.971
AHU 4 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 1 | 0% | 0% | 0 | 0 | 0
| 92.5 | 4 | 0% | 0% | 0 | 0 | 0
| 87.5 | 17 | 0% | 0% | 0 | 0 | 0
| 82.5 | 47 | 0% | 0% | 0 | 0 | 0
| 77.5 | 156 | 0% | 0% | 0 | 0 | 0
| 72.5 | 374 | 0% | 0% | 0 | 0 | 0
| 67.5 | 440 | 0% | 0% | 0 | 0 | 0
| 62.5 | 364 | 3.704% | 0% | 13.4815 | 0 | 13.4815
| 57.5 | 347 | 11.11% | 0% | 38.5556 | 0 | 38.5556
| 52.5 | 364 | 18.52% | 4.348% | 67.4074 | 15.8261 | 51.5813
| 47.5 | 268 | 25.93% | 13.04% | 69.4815 | 34.9565 | 34.525
| 42.5 | 392 | 33.33% | 21.74% | 130.6667 | 85.2174 | 45.4493
| 37.5 | 329 | 40.74% | 30.43% | 134.037 | 100.1304 | 33.9066
| 32.5 | 238 | 48.15% | 39.13% | 114.5926 | 93.1304 | 21.4622
| 27.5 | 152 | 55.56% | 47.83% | 84.4444 | 72.6957 | 11.7488
| 22.5 | 130 | 62.96% | 56.52% | 81.8519 | 73.4783 | 8.3736
| 17.5 | 86 | 70.37% | 65.22% | 60.5185 | 56.087 | 4.4316
| 12.5 | 32 | 77.78% | 73.91% | 24.8889 | 23.6522 | 1.2367
| 7.5 | 7 | 85.19% | 82.61% | 5.963 | 5.7826 | 0.18035
| 2.5 | 3 | 92.59% | 91.3% | 2.7778 | 2.7391 | 0.038647
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 3751 |  |  |  | Totals | 264.971
AHU 5 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 1 | 0% | 0% | 0 | 0 | 0
| 92.5 | 4 | 0% | 0% | 0 | 0 | 0
| 87.5 | 17 | 0% | 0% | 0 | 0 | 0
| 82.5 | 47 | 0% | 0% | 0 | 0 | 0
| 77.5 | 156 | 0% | 0% | 0 | 0 | 0
| 72.5 | 374 | 0% | 0% | 0 | 0 | 0
| 67.5 | 440 | 0% | 0% | 0 | 0 | 0
| 62.5 | 364 | 3.704% | 0% | 13.4815 | 0 | 13.4815
| 57.5 | 347 | 11.11% | 0% | 38.5556 | 0 | 38.5556
| 52.5 | 364 | 18.52% | 4.348% | 67.4074 | 15.8261 | 51.5813
| 47.5 | 268 | 25.93% | 13.04% | 69.4815 | 34.9565 | 34.525
| 42.5 | 392 | 33.33% | 21.74% | 130.6667 | 85.2174 | 45.4493
| 37.5 | 329 | 40.74% | 30.43% | 134.037 | 100.1304 | 33.9066
| 32.5 | 238 | 48.15% | 39.13% | 114.5926 | 93.1304 | 21.4622
| 27.5 | 152 | 55.56% | 47.83% | 84.4444 | 72.6957 | 11.7488
| 22.5 | 130 | 62.96% | 56.52% | 81.8519 | 73.4783 | 8.3736
| 17.5 | 86 | 70.37% | 65.22% | 60.5185 | 56.087 | 4.4316
| 12.5 | 32 | 77.78% | 73.91% | 24.8889 | 23.6522 | 1.2367
| 7.5 | 7 | 85.19% | 82.61% | 5.963 | 5.7826 | 0.18035
| 2.5 | 3 | 92.59% | 91.3% | 2.7778 | 2.7391 | 0.038647
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 3751 |  |  |  | Totals | 264.971
AHU 6 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0% | 0% | 0 | 0 | 0
| 67.5 | 126 | 6.04% | 0% | 7.6107 | 0 | 7.6107
| 62.5 | 94 | 12.75% | 0% | 11.9866 | 0 | 11.9866
| 57.5 | 111 | 19.46% | 0% | 21.604 | 0 | 21.604
| 52.5 | 109 | 26.17% | 4.348% | 28.5302 | 4.7391 | 23.7911
| 47.5 | 68 | 32.89% | 13.04% | 22.3624 | 8.8696 | 13.4929
| 42.5 | 132 | 39.6% | 21.74% | 52.2685 | 28.6957 | 23.5728
| 37.5 | 111 | 46.31% | 30.43% | 51.4027 | 33.7826 | 17.6201
| 32.5 | 81 | 53.02% | 39.13% | 42.9463 | 31.6957 | 11.2507
| 27.5 | 44 | 59.73% | 47.83% | 26.2819 | 21.0435 | 5.2384
| 22.5 | 46 | 66.44% | 56.52% | 30.5638 | 26 | 4.5638
| 17.5 | 25 | 73.15% | 65.22% | 18.2886 | 16.3043 | 1.9842
| 12.5 | 14 | 79.87% | 73.91% | 11.1812 | 10.3478 | 0.83338
| 7.5 | 4 | 86.58% | 82.61% | 3.4631 | 3.3043 | 0.15874
| 2.5 | 3 | 93.29% | 91.3% | 2.7987 | 2.7391 | 0.059527
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 136.1561
AHU 7 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0% | 0% | 0 | 0 | 0
| 67.5 | 126 | 0% | 0% | 0 | 0 | 0
| 62.5 | 94 | 0% | 0% | 0 | 0 | 0
| 57.5 | 111 | 4% | 0% | 4.44 | 0 | 4.44
| 52.5 | 109 | 12% | 4.348% | 13.08 | 4.7391 | 8.3409
| 47.5 | 68 | 20% | 13.04% | 13.6 | 8.8696 | 4.7304
| 42.5 | 132 | 28% | 21.74% | 36.96 | 28.6957 | 8.2643
| 37.5 | 111 | 36% | 30.43% | 39.96 | 33.7826 | 6.1774
| 32.5 | 81 | 44% | 39.13% | 35.64 | 31.6957 | 3.9443
| 27.5 | 44 | 52% | 47.83% | 22.88 | 21.0435 | 1.8365
| 22.5 | 46 | 60% | 56.52% | 27.6 | 26 | 1.6
| 17.5 | 25 | 68% | 65.22% | 17 | 16.3043 | 0.69565
| 12.5 | 14 | 76% | 73.91% | 10.64 | 10.3478 | 0.29217
| 7.5 | 4 | 84% | 82.61% | 3.36 | 3.3043 | 0.055652
| 2.5 | 3 | 92% | 91.3% | 2.76 | 2.7391 | 0.02087
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 40.3983
AHU 8 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 1 | 0% | 0% | 0 | 0 | 0
| 82.5 | 5 | 0% | 0% | 0 | 0 | 0
| 77.5 | 88 | 0% | 0% | 0 | 0 | 0
| 72.5 | 281 | 0% | 0% | 0 | 0 | 0
| 67.5 | 332 | 0% | 0% | 0 | 0 | 0
| 62.5 | 290 | 0% | 0% | 0 | 0 | 0
| 57.5 | 276 | 4% | 0% | 11.04 | 0 | 11.04
| 52.5 | 269 | 12% | 4.348% | 32.28 | 11.6957 | 20.5843
| 47.5 | 203 | 20% | 13.04% | 40.6 | 26.4783 | 14.1217
| 42.5 | 343 | 28% | 21.74% | 96.04 | 74.5652 | 21.4748
| 37.5 | 290 | 36% | 30.43% | 104.4 | 88.2609 | 16.1391
| 32.5 | 191 | 44% | 39.13% | 84.04 | 74.7391 | 9.3009
| 27.5 | 120 | 52% | 47.83% | 62.4 | 57.3913 | 5.0087
| 22.5 | 116 | 60% | 56.52% | 69.6 | 65.5652 | 4.0348
| 17.5 | 66 | 68% | 65.22% | 44.88 | 43.0435 | 1.8365
| 12.5 | 40 | 76% | 73.91% | 30.4 | 29.5652 | 0.83478
| 7.5 | 7 | 84% | 82.61% | 5.88 | 5.7826 | 0.097391
| 2.5 | 3 | 92% | 91.3% | 2.76 | 2.7391 | 0.02087
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 2921 |  |  |  | Totals | 104.4939
AHU 9 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0% | 0% | 0 | 0 | 0
| 67.5 | 126 | 0% | 0% | 0 | 0 | 0
| 62.5 | 94 | 0% | 0% | 0 | 0 | 0
| 57.5 | 111 | 4% | 0% | 4.44 | 0 | 4.44
| 52.5 | 109 | 12% | 4.348% | 13.08 | 4.7391 | 8.3409
| 47.5 | 68 | 20% | 13.04% | 13.6 | 8.8696 | 4.7304
| 42.5 | 132 | 28% | 21.74% | 36.96 | 28.6957 | 8.2643
| 37.5 | 111 | 36% | 30.43% | 39.96 | 33.7826 | 6.1774
| 32.5 | 81 | 44% | 39.13% | 35.64 | 31.6957 | 3.9443
| 27.5 | 44 | 52% | 47.83% | 22.88 | 21.0435 | 1.8365
| 22.5 | 46 | 60% | 56.52% | 27.6 | 26 | 1.6
| 17.5 | 25 | 68% | 65.22% | 17 | 16.3043 | 0.69565
| 12.5 | 14 | 76% | 73.91% | 10.64 | 10.3478 | 0.29217
| 7.5 | 4 | 84% | 82.61% | 3.36 | 3.3043 | 0.055652
| 2.5 | 3 | 92% | 91.3% | 2.76 | 2.7391 | 0.02087
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 40.3983
AHU 10 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0% | 0% | 0 | 0 | 0
| 67.5 | 126 | 0% | 0% | 0 | 0 | 0
| 62.5 | 94 | 0% | 0% | 0 | 0 | 0
| 57.5 | 111 | 4% | 0% | 4.44 | 0 | 4.44
| 52.5 | 109 | 12% | 4.348% | 13.08 | 4.7391 | 8.3409
| 47.5 | 68 | 20% | 13.04% | 13.6 | 8.8696 | 4.7304
| 42.5 | 132 | 28% | 21.74% | 36.96 | 28.6957 | 8.2643
| 37.5 | 111 | 36% | 30.43% | 39.96 | 33.7826 | 6.1774
| 32.5 | 81 | 44% | 39.13% | 35.64 | 31.6957 | 3.9443
| 27.5 | 44 | 52% | 47.83% | 22.88 | 21.0435 | 1.8365
| 22.5 | 46 | 60% | 56.52% | 27.6 | 26 | 1.6
| 17.5 | 25 | 68% | 65.22% | 17 | 16.3043 | 0.69565
| 12.5 | 14 | 76% | 73.91% | 10.64 | 10.3478 | 0.29217
| 7.5 | 4 | 84% | 82.61% | 3.36 | 3.3043 | 0.055652
| 2.5 | 3 | 92% | 91.3% | 2.76 | 2.7391 | 0.02087
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 40.3983
AHU 11 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 12 | 0% | 0% | 0 | 0 | 0
| 92.5 | 53 | 0% | 0% | 0 | 0 | 0
| 87.5 | 106 | 0% | 0% | 0 | 0 | 0
| 82.5 | 237 | 0% | 0% | 0 | 0 | 0
| 77.5 | 418 | 0% | 0% | 0 | 0 | 0
| 72.5 | 543 | 3.226% | 0% | 17.5161 | 0 | 17.5161
| 67.5 | 586 | 9.677% | 0% | 56.7097 | 0 | 56.7097
| 62.5 | 563 | 16.13% | 0% | 90.8065 | 0 | 90.8065
| 57.5 | 510 | 22.58% | 0% | 115.1613 | 0 | 115.1613
| 52.5 | 517 | 29.03% | 4.348% | 150.0968 | 22.4783 | 127.6185
| 47.5 | 368 | 35.48% | 13.04% | 130.5806 | 48 | 82.5806
| 42.5 | 568 | 41.94% | 21.74% | 238.1935 | 123.4783 | 114.7153
| 37.5 | 433 | 48.39% | 30.43% | 209.5161 | 131.7826 | 77.7335
| 32.5 | 344 | 54.84% | 39.13% | 188.6452 | 134.6087 | 54.0365
| 27.5 | 199 | 61.29% | 47.83% | 121.9677 | 95.1739 | 26.7938
| 22.5 | 162 | 67.74% | 56.52% | 109.7419 | 91.5652 | 18.1767
| 17.5 | 108 | 74.19% | 65.22% | 80.129 | 70.4348 | 9.6942
| 12.5 | 40 | 80.65% | 73.91% | 32.2581 | 29.5652 | 2.6928
| 7.5 | 8 | 87.1% | 82.61% | 6.9677 | 6.6087 | 0.35905
| 2.5 | 3 | 93.55% | 91.3% | 2.8065 | 2.7391 | 0.067321
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 5778 |  |  |  | Totals | 720.4362
AHU 12 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0% | 0% | 0 | 0 | 0
| 67.5 | 126 | 3.448% | 0% | 4.3448 | 0 | 4.3448
| 62.5 | 94 | 10.34% | 0% | 9.7241 | 0 | 9.7241
| 57.5 | 111 | 17.24% | 0% | 19.1379 | 0 | 19.1379
| 52.5 | 109 | 24.14% | 4.348% | 26.3103 | 4.7391 | 21.5712
| 47.5 | 68 | 31.03% | 13.04% | 21.1034 | 8.8696 | 12.2339
| 42.5 | 132 | 37.93% | 21.74% | 50.069 | 28.6957 | 21.3733
| 37.5 | 111 | 44.83% | 30.43% | 49.7586 | 33.7826 | 15.976
| 32.5 | 81 | 51.72% | 39.13% | 41.8966 | 31.6957 | 10.2009
| 27.5 | 44 | 58.62% | 47.83% | 25.7931 | 21.0435 | 4.7496
| 22.5 | 46 | 65.52% | 56.52% | 30.1379 | 26 | 4.1379
| 17.5 | 25 | 72.41% | 65.22% | 18.1034 | 16.3043 | 1.7991
| 12.5 | 14 | 79.31% | 73.91% | 11.1034 | 10.3478 | 0.75562
| 7.5 | 4 | 86.21% | 82.61% | 3.4483 | 3.3043 | 0.14393
| 2.5 | 3 | 93.1% | 91.3% | 2.7931 | 2.7391 | 0.053973
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 121.8576
AHU 13 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 1.639% | 0% | 0 | 0 | 0
| 82.5 | 0 | 7.104% | 0% | 0 | 0 | 0
| 77.5 | 25 | 12.57% | 0% | 3.1421 | 0 | 3.1421
| 72.5 | 103 | 18.03% | 0% | 18.5738 | 0 | 18.5738
| 67.5 | 126 | 23.5% | 0% | 29.6066 | 0 | 29.6066
| 62.5 | 94 | 28.96% | 0% | 27.224 | 0 | 27.224
| 57.5 | 111 | 34.43% | 0% | 38.2131 | 0 | 38.2131
| 52.5 | 109 | 39.89% | 4.348% | 43.4809 | 4.7391 | 38.7417
| 47.5 | 68 | 45.36% | 13.04% | 30.8415 | 8.8696 | 21.972
| 42.5 | 132 | 50.82% | 21.74% | 67.082 | 28.6957 | 38.3863
| 37.5 | 111 | 56.28% | 30.43% | 62.4754 | 33.7826 | 28.6928
| 32.5 | 81 | 61.75% | 39.13% | 50.0164 | 31.6957 | 18.3207
| 27.5 | 44 | 67.21% | 47.83% | 29.5738 | 21.0435 | 8.5303
| 22.5 | 46 | 72.68% | 56.52% | 33.4317 | 26 | 7.4317
| 17.5 | 25 | 78.14% | 65.22% | 19.5355 | 16.3043 | 3.2312
| 12.5 | 14 | 83.61% | 73.91% | 11.7049 | 10.3478 | 1.3571
| 7.5 | 4 | 89.07% | 82.61% | 3.5628 | 3.3043 | 0.25849
| 2.5 | 3 | 94.54% | 91.3% | 2.8361 | 2.7391 | 0.096935
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 232.4564
AHU 14 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 2 | 0% | 0% | 0 | 0 | 0
| 87.5 | 11 | 0% | 0% | 0 | 0 | 0
| 82.5 | 102 | 0% | 0% | 0 | 0 | 0
| 77.5 | 290 | 0% | 0% | 0 | 0 | 0
| 72.5 | 337 | 0% | 0% | 0 | 0 | 0
| 67.5 | 297 | 0% | 0% | 0 | 0 | 0
| 62.5 | 269 | 0% | 0% | 0 | 0 | 0
| 57.5 | 262 | 4% | 0% | 10.48 | 0 | 10.48
| 52.5 | 213 | 12% | 4.348% | 25.56 | 9.2609 | 16.2991
| 47.5 | 338 | 20% | 13.04% | 67.6 | 44.087 | 23.513
| 42.5 | 273 | 28% | 21.74% | 76.44 | 59.3478 | 17.0922
| 37.5 | 184 | 36% | 30.43% | 66.24 | 56 | 10.24
| 32.5 | 123 | 44% | 39.13% | 54.12 | 48.1304 | 5.9896
| 27.5 | 111 | 52% | 47.83% | 57.72 | 53.087 | 4.633
| 22.5 | 64 | 60% | 56.52% | 38.4 | 36.1739 | 2.2261
| 17.5 | 37 | 68% | 65.22% | 25.16 | 24.1304 | 1.0296
| 12.5 | 5 | 76% | 73.91% | 3.8 | 3.6957 | 0.10435
| 7.5 | 3 | 84% | 82.61% | 2.52 | 2.4783 | 0.041739
| 2.5 | 0 | 92% | 91.3% | 0 | 0 | 0
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 2921 |  |  |  | Totals | 91.6487
AHU 15 | AHU 1: Temp Mid-Point (T1); AHU 2: RTU Unoccupied Bin Hours; AHU 3: Baseline Equivalent Full Load Hours (%) at Each Bin; AHU 4: Proposed Equivalent Full Load Hours (%) at Each Bin; AHU 5: Baseline Total Full Load Operating Hours; AHU 6: Proposed Total Full Load Operating Hours; AHU 7: Total Reduction in Operating Hours
| 102.5 | 0 | 0% | 0% | 0 | 0 | 0
| 97.5 | 0 | 0% | 0% | 0 | 0 | 0
| 92.5 | 0 | 0% | 0% | 0 | 0 | 0
| 87.5 | 0 | 0% | 0% | 0 | 0 | 0
| 82.5 | 0 | 0% | 0% | 0 | 0 | 0
| 77.5 | 25 | 0% | 0% | 0 | 0 | 0
| 72.5 | 103 | 0% | 0% | 0 | 0 | 0
| 67.5 | 126 | 0% | 0% | 0 | 0 | 0
| 62.5 | 94 | 0% | 0% | 0 | 0 | 0
| 57.5 | 111 | 4% | 0% | 4.44 | 0 | 4.44
| 52.5 | 109 | 12% | 4.348% | 13.08 | 4.7391 | 8.3409
| 47.5 | 68 | 20% | 13.04% | 13.6 | 8.8696 | 4.7304
| 42.5 | 132 | 28% | 21.74% | 36.96 | 28.6957 | 8.2643
| 37.5 | 111 | 36% | 30.43% | 39.96 | 33.7826 | 6.1774
| 32.5 | 81 | 44% | 39.13% | 35.64 | 31.6957 | 3.9443
| 27.5 | 44 | 52% | 47.83% | 22.88 | 21.0435 | 1.8365
| 22.5 | 46 | 60% | 56.52% | 27.6 | 26 | 1.6
| 17.5 | 25 | 68% | 65.22% | 17 | 16.3043 | 0.69565
| 12.5 | 14 | 76% | 73.91% | 10.64 | 10.3478 | 0.29217
| 7.5 | 4 | 84% | 82.61% | 3.36 | 3.3043 | 0.055652
| 2.5 | 3 | 92% | 91.3% | 2.76 | 2.7391 | 0.02087
| -2.5 | 0 | 100% | 100% | 0 | 0 | 0
|  | 1096 |  |  |  | Totals | 40.3983

## ECM4 (2) (hidden)
ECM- |  |  |  | 4 | Optimize Differential Pressure Set point reset with reduction in OAT Lockout
Input Variables | [5 empty] | Equations & Variables
Cost of Electricity ($/ kwh) |  | 0.12 | 0.12 |  |  | Electric Energy Equation (kWh) | =((HP*Mtr Load %*.746)/(Mtr Eff * VFD eff)) * VFD Speed^fan law exponent
Maximum RPM |  | 1800 | 1800 |  |  | Pump RPM = | =(Current bin temp.-Lowest bin temp)/(Highest bin temp.-Lowest bin temp)*Pump Max RPM
Minimum RPM | 0.6 | 720 | 720
AHU Equipment Values | RTU # 1 | 0
Tonnage | 15 | 0
Motor Load Factor | 65% | 65%
Motor Efficiency | 86.5% | 86.5%
VFD Efficiency | 90% | 90%
Pump Law exponent | 2.5 | 2.5
Pump Law exponent (proposed) | 3 | 3
Pump Max RPM | 1800 | 1800
Pump Min RPM | 720 | 720
| Fan Savings (KWh) | Cost Savings ($)
RTU # 1 | 6886.6752 | 826.401
0 | 0 | 0
Totals | 6886.6752 | 826.401
Total Electric Savings
| kHw | 6886.6752
| Dollars | 826.401
RTU # 1 | [6 empty] | 0
Temp Mid-Point (T1) | Bin Hours Existing | Supply pump RPM (Proposed) | Supply Fan VFD Speed @ each bin (Proposed) | kWh Consumption (Existing) | kWh Consumption (Proposed) | kWh Saved | Temp Mid-Point (T1) | Bin Hours Existing | Supply pump GPM (Proposed) | Supply Fan VFD Speed @ each bin (Proposed) | kWh Consumption (Existing) | kWh Consumption (Proposed) | kWh Saved
97.5 | #REF! | #REF! | #REF! |  |  |  | 97.5 | #REF! | #REF! | #REF!
92.5 | #REF! | #REF! | #REF! |  |  |  | 92.5 | #REF! | #REF! | #REF!
87.5 | #REF! | #REF! | #REF! |  |  |  | 87.5 | #REF! | #REF! | #REF!
82.5 | #REF! | #REF! | #REF! |  |  |  | 82.5 | #REF! | #REF! | #REF!
77.5 | #REF! | #REF! | #REF! |  |  |  | 77.5 | #REF! | #REF! | #REF!
72.5 | #REF! | #REF! | #REF! |  |  |  | 72.5 | #REF! | #REF! | #REF!
67.5 | #REF! | #REF! | #REF! |  |  |  | 67.5 | #REF! | #REF! | #REF!
62.5 | #REF! | #REF! | #REF! |  |  |  | 62.5 | #REF! | #REF! | #REF!
97.5 | 4 | 720 | 40% | 3.7818 |  | 3.7818 | 97.5 | 4 | 720 | 40% | 0 |  | 0
92.5 | 94 | 720 | 40% | 88.8715 |  | 88.8715 | 92.5 | 94 | 720 | 40% | 0 |  | 0
87.5 | 239 | 720 | 40% | 225.9606 |  | 225.9606 | 87.5 | 239 | 720 | 40% | 0 |  | 0
82.5 | 492 | 720 | 40% | 465.1574 |  | 465.1574 | 82.5 | 492 | 720 | 40% | 0 |  | 0
77.5 | 695 | 720 | 40% | 657.0821 |  | 657.0821 | 77.5 | 695 | 720 | 40% | 0 |  | 0
72.5 | 753 | 720 | 40% | 711.9177 |  | 711.9177 | 72.5 | 753 | 720 | 40% | 0 |  | 0
67.5 | 762 | 720 | 40% | 720.4267 |  | 720.4267 | 67.5 | 762 | 720 | 40% | 0 |  | 0
62.5 | 903 | 720 | 40% | 853.734 |  | 853.734 | 62.5 | 903 | 720 | 40% | 0 |  | 0
57.5 | 721 | 800 | 44.44% | 887.0821 |  | 887.0821 | 57.5 | 721 | 800 | 44.44% | 0 |  | 0
52.5 | 813 | 900 | 50% | 1342.7661 | 949.479 | 393.2871 | 52.5 | 813 | 900 | 50% | 0 | 0 | 0
47.5 | 583 | 1000 | 55.56% | 1253.0607 | 933.9763 | 319.0844 | 47.5 | 583 | 1000 | 55.56% | 0 | 0 | 0
42.5 | 632 | 1100 | 61.11% | 1723.8614 | 1347.6045 | 376.257 | 42.5 | 632 | 1100 | 61.11% | 0 | 0 | 0
37.5 | 756 | 1200 | 66.67% | 2563.1763 | 2092.8247 | 470.3516 | 37.5 | 756 | 1200 | 66.67% | 0 | 0 | 0
32.5 | 540 | 1300 | 72.22% | 2236.432 | 1900.6018 | 335.8303 | 32.5 | 540 | 1300 | 72.22% | 0 | 0 | 0
27.5 | 336 | 1400 | 77.78% | 1674.7999 | 1477.0347 | 197.7652 | 27.5 | 336 | 1400 | 77.78% | 0 | 0 | 0
22.5 | 214 | 1500 | 83.33% | 1267.4928 | 1157.0573 | 110.4355 | 22.5 | 214 | 1500 | 83.33% | 0 | 0 | 0
17.5 | 136 | 1600 | 88.89% | 946.5475 | 892.4136 | 54.134 | 17.5 | 136 | 1600 | 88.89% | 0 | 0 | 0
12.5 | 68 | 1700 | 94.44% | 550.725 | 535.2085 | 15.5165 | 12.5 | 68 | 1700 | 94.44% | 0 | 0 | 0
7.5 | 19 | 1800 | 100% | 177.5164 | 177.5164 | 0 | 7.5 | 19 | 1800 | 100% | 0 | 0 | 0
|  |  |  | TOTAL |  | 6886.6752 |  |  |  |  | TOTAL |  | 0
| RPM calculation | [5 empty] | RPM calculation
| Chilled water Pump | % Usage |  |  |  |  | Chilled water Pump | % Usage
| 720 | 40 |  |  |  |  | 720 | 40
| 720 | 40 |  |  |  |  | 720 | 40
| 720 | 40 |  |  |  |  | 720 | 40
| 720 | 40 |  |  |  |  | 720 | 40
| 720 | 40 |  |  |  |  | 720 | 40
| 720 | 40 |  |  |  |  | 720 | 40
| 720 | 40 |  |  |  |  | 720 | 40
| 720 | 40 |  |  |  |  | 720 | 40
| 800 | 44.4444 |  |  |  |  | 800 | 44.4444
| 900 | 50 |  |  |  |  | 900 | 50
| 1000 | 55.5556 |  |  |  |  | 1000 | 55.5556
| 1100 | 61.1111 |  |  |  |  | 1100 | 61.1111
| 1200 | 66.6667 |  |  |  |  | 1200 | 66.6667
| 1300 | 72.2222 |  |  |  |  | 1300 | 72.2222
| 1400 | 77.7778 |  |  |  |  | 1400 | 77.7778
| 1500 | 83.3333 |  |  |  |  | 1500 | 83.3333
| 1600 | 88.8889 |  |  |  |  | 1600 | 88.8889
| 1700 | 94.4444 |  |  |  |  | 1700 | 94.4444
| 1800 | 100 |  |  |  |  | 1800 | 100

## TMY3 DATA (Schedule - HVAC)
SCHEDULE
|  | EXISTING | [28 empty] | PROPOSED
|  | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | Existing Operating Schedule | [21 empty] | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | Proposed Operating Schedule | RTU Equivalent Full Load Hours (%) at Each Bin | RTU Equivalent Full Load Hours (%) at Each Bin (PROPOSED)
|  | AHU #1 | AHU #2 | AHU #3 | AHU #4 | AHU #5 | AHU #6 | AHU #7 | RTU # 1 | [21 empty] | AHU #1 | AHU #2 | AHU #3 | AHU #4 | AHU #5 | AHU #6 | AHU #7 | RTU # 1 |  |  | EXISTING HVAC SCHEDULE | [15 empty] | EXISTING BIN HOURS | [15 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | [21 empty] | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Percent % | Percent % | [32 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2
102.5 | 100 to 105 | 3 | 2 | 5 | 5 | 3 | 3 | 3 | 3 | [21 empty] | 3 | 2 | 0 | 5 | 3 | 3 | 3 | 3 | 100% | 0% | AHU #1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #7 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #7 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 3 | 3 | 3 | 3 | 3 | 3 | 3
97.5 | 95 to 100 | 28 | 2 | 40 | 40 | 28 | 5 | 28 | 28 | [21 empty] | 26 | 2 | 0 | 40 | 26 | 5 | 26 | 28 | 100% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 4 | 4 | 4 | 4 | 4 | 4 | 4
92.5 | 90 to 95 | 72 | 6 | 229 | 229 | 70 | 20 | 70 | 72 | [21 empty] | 67 | 6 | 2 | 229 | 67 | 20 | 67 | 72 | 88.24% | 0% | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 19:00 | 19:00 | 19:00 | 19:00 | 19:00 | 19:00 | 19:00 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 5 | 5 | 5 | 5 | 5 | 5 | 5
87.5 | 85 to 90 | 192 | 20 | 435 | 435 | 184 | 39 | 184 | 192 | [21 empty] | 172 | 20 | 11 | 435 | 172 | 39 | 172 | 192 | 76.47% | 0% | [32 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6
82.5 | 80 to 85 | 420 | 37 | 713 | 713 | 384 | 48 | 384 | 420 | [21 empty] | 354 | 37 | 77 | 713 | 356 | 48 | 356 | 420 | 64.71% | 0% | AHU #2 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | RTU # 1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #2 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | RTU # 1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 7 | 7 | 7 | 7 | 7 | 7 | 7
77.5 | 75 to 80 | 649 | 20 | 775 | 775 | 476 | 41 | 476 | 649 | [21 empty] | 419 | 20 | 187 | 775 | 440 | 41 | 440 | 649 | 52.94% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 8:00 | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 800 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8
72.5 | 70 to 75 | 819 | 23 | 1091 | 1091 | 385 | 30 | 385 | 819 | [21 empty] | 303 | 23 | 211 | 1091 | 344 | 30 | 344 | 819 | 41.18% | 0% | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 13:00 | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 9 | 9 | 9 | 9 | 9 | 9 | 9
67.5 | 65 to 70 | 873 | 14 | 1039 | 1039 | 364 | 21 | 364 | 873 | [21 empty] | 292 | 14 | 203 | 1039 | 325 | 21 | 325 | 873 | 29.41% | 0% | [32 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10
62.5 | 60 to 65 | 782 | 15 | 894 | 894 | 354 | 39 | 354 | 782 | [21 empty] | 301 | 15 | 158 | 894 | 334 | 39 | 334 | 782 | 17.65% | 0% | AHU #3 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #3 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 11 | 11 | 11 | 11 | 11 | 11 | 11
57.5 | 55 to 60 | 768 | 30 | 759 | 759 | 379 | 42 | 379 | 768 | [21 empty] | 313 | 30 | 153 | 759 | 346 | 42 | 346 | 768 | 5.882% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12
52.5 | 50 to 55 | 795 | 21 | 640 | 640 | 369 | 23 | 369 | 795 | [21 empty] | 300 | 21 | 145 | 640 | 337 | 23 | 337 | 795 | 3.333% | 0% | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 13 | 13 | 13 | 13 | 13 | 13 | 13
47.5 | 45 to 50 | 551 | 24 | 671 | 671 | 255 | 37 | 255 | 551 | [21 empty] | 210 | 24 | 206 | 671 | 229 | 37 | 229 | 551 | 10% | 0% | [32 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14
42.5 | 40 to 45 | 858 | 11 | 673 | 673 | 357 | 18 | 357 | 858 | [21 empty] | 290 | 11 | 162 | 673 | 328 | 18 | 328 | 858 | 16.67% | 0% | AHU #4 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #4 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 15 | 15 | 15 | 15 | 15 | 15 | 15
37.5 | 35 to 40 | 651 | 11 | 287 | 287 | 245 | 14 | 245 | 651 | [21 empty] | 195 | 11 | 103 | 287 | 227 | 14 | 227 | 651 | 23.33% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16
32.5 | 30 to 35 | 476 | 3 | 196 | 196 | 214 | 6 | 214 | 476 | [21 empty] | 164 | 3 | 79 | 196 | 193 | 6 | 193 | 476 | 30% | 0% | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 17 | 17 | 17 | 17 | 17 | 17 | 17
27.5 | 25 to 30 | 283 | 10 | 214 | 214 | 101 | 16 | 101 | 283 | [21 empty] | 80 | 10 | 65 | 214 | 93 | 16 | 93 | 283 | 36.67% | 0% | [32 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18
22.5 | 20 to 25 | 277 | 6 | 83 | 83 | 118 | 9 | 118 | 277 | [21 empty] | 95 | 6 | 39 | 83 | 108 | 9 | 108 | 277 | 43.33% | 0% | AHU #5 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | AHU #5 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19
17.5 | 15 to 20 | 178 | 5 | 10 | 10 | 71 | 5 | 71 | 178 | [21 empty] | 52 | 5 | 23 | 10 | 65 | 5 | 65 | 178 | 50% | 0% | Start | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | [8 empty] | Start | 700 | 700 | 700 | 700 | 700 | 700 | 700 | [8 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20
12.5 | 10 to 15 | 71 | 0 | 5 | 5 | 19 | 0 | 19 | 71 | [21 empty] | 13 | 0 | 1 | 5 | 18 | 0 | 18 | 71 | 56.67% | 0% | Stop | 19:00 | 19:00 | 19:00 | 19:00 | 19:00 | 19:00 | 19:00 | [8 empty] | Stop | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | [8 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21
7.5 | 5 to 10 | 9 | 0 | 1 | 1 | 2 | 0 | 2 | 9 | [21 empty] | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 9 | 63.33% | 0% | [32 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22
2.5 | 0 to 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | [21 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 4 | 70% | 0% | AHU #6 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | AHU #6 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23
-2.5 | -5 to 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [21 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 76.67% | 0% | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 8:00 | [8 empty] | Start | 0 | 0 | 0 | 0 | 0 | 0 | 800 | [8 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | 8760 | 260 | 8760 | 8760 | 4378 | 416 | 4378 | 8760 | [21 empty] | 3650 | 260 | 1825 | 8760 | 4015 | 416 | 4015 | 8760 |  |  | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 16:00 | [8 empty] | Stop | 0 | 0 | 0 | 0 | 0 | 0 | 1500
|  | 8760 | 260 | 8760 | 8760 | 4378 | 416 | 4378 | 8760 | [21 empty] | 3650 | 260 | 1825 | 8760 | 4015 | 416 | 4015 | 8760
|  | YES | YES | YES | YES | YES | YES | YES | YES | [21 empty] | YES | YES | YES | YES | YES | YES | YES | YES |  |  | PROPOSED HVAC SCHEDULE | [15 empty] | PROPOSED BIN HOURS
RTU Load Profile |  | AHU #3: RTU Load Profile (Proposed) | [31 empty] | AHU #1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #7 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #7 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
OAT | EFLCH % | AHU #1: EFLHH %; AHU #3: OAT; AHU #4: EFLCH %; AHU #5: EFLHH % | [31 empty] | Start | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | Start | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | Start | 800 | 800 | 800 | 800 | 800 | 800 | 800 | Start | 700 | 700 | 700 | 700 | 700 | 700 | 700
97.5 | 100% | AHU #3: 97.5; AHU #4: 0% | [31 empty] | Stop | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | Stop | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | Stop | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | Stop | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700
55 | 0% | AHU #3: 55; AHU #4: 0%
55 |  | AHU #1: 0%; AHU #3: 55; AHU #5: 0% | Reduction In Operating Hours | [30 empty] | AHU #2 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | RTU # 1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #2 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | RTU # 1 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
2.5 |  | 70% |  | 7.5 |  | 0% |  |  |  | AHU #1 | AHU #2 | AHU #3 | AHU #4 | AHU #5 | AHU #6 | AHU #7 | RTU # 1 | [23 empty] | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 8:00 | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 800 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slope | 0.023529 | -0.013333 |  | Slope | 0 | 0 |  |  |  | 5110 | 0 | 6935 | 0 | 363 | 0 | 363 | 0 | [23 empty] | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 13:00 | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400
Intercept | -1.2941 | 0.73333 |  | Intercept | 0 | 0
[41 empty] | AHU #3 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #3 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
[41 empty] | Start | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0
Conventional Binning :Conventional Bins for BALTIMORE BLT-WASHNGTN INT'L MD USFA #: 724060TY | [40 empty] | Stop | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | 2:00 | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400
BALTIMORE BLT-WASHNGTN INT'L, MD; USAF#: 724060TY; Altitude: 45 meters / 148 ft; Latitude: 39.167; Longitude: -76.683
Units: | I-P | 724060TY | BALTIMORE BLT-WASHNGTN INT'L, MD |  |  | 39.167 | -76.683 | 147.6378 ft | [32 empty] | AHU #4 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | AHU #4 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | 0 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
[41 empty] | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Start | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU #1 | [40 empty] | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | Stop | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | Stop | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stop | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [20 empty] | AHU #5 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | AHU #5 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [14 empty] | Start | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | [8 empty] | Start | 700 | 700 | 700 | 700 | 700 | 700 | 700
Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | Reduction In Operating Hours AHU #1: 1; Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 800 | 1800 | 1800 | [21 empty] | Stop | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | 18:00 | [8 empty] | Stop | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700
Monday | 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 800 | 1800 | 1800
Tuesday | 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | Reduction In Operating Hours AHU #1: 3; Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 800 | 1800 | 1800 | [21 empty] | AHU #6 | Sun | Mon | Tue | Wed | Thu | Fri | Sat | [8 empty] | AHU #6 | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Wednesday | 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | Reduction In Operating Hours AHU #1: 4; Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 800 | 1800 | 1800 | [21 empty] | Start | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 12:00 AM | 8:00 | [8 empty] | Start | 0 | 0 | 0 | 0 | 0 | 0 | 800
Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | Reduction In Operating Hours AHU #1: 5; Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 800 | 1800 | 1800 | [21 empty] | Stop | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 1:00 | 16:00 | [8 empty] | Stop | 0 | 0 | 0 | 0 | 0 | 0 | 1500
Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | Reduction In Operating Hours AHU #1: 6; Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 800 | 1800 | 1800
Saturday | 100 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | Reduction In Operating Hours AHU #1: 7; Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 800 | 1800 | 1800
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | Reduction In Operating Hours AHU #1: 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | Reduction In Operating Hours AHU #1: 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | Reduction In Operating Hours AHU #1: 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 800 | 1800 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 800 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 800 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 800 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | Reduction In Operating Hours AHU #1: 16; Reduction In Operating Hours RTU # 1: 800 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | Reduction In Operating Hours AHU #1: 17; Reduction In Operating Hours RTU # 1: 800 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | Reduction In Operating Hours AHU #1: 18; Reduction In Operating Hours RTU # 1: 800 | 1800
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | Reduction In Operating Hours AHU #1: 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | Reduction In Operating Hours AHU #1: 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | Reduction In Operating Hours AHU #1: 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | Reduction In Operating Hours AHU #1: 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | Reduction In Operating Hours AHU #1: 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | Reduction In Operating Hours AHU #1: 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | Reduction In Operating Hours AHU #7: 102.5; Reduction In Operating Hours RTU # 1: 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 26 | [5 empty] | 8 | 18
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 67 | [5 empty] | 31 | 34 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | Reduction In Operating Hours AHU #1: 33; Reduction In Operating Hours AHU #2: 12; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 172 |  |  |  |  | 6 | 66 | 56 | 32 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 354 |  |  |  |  | 45 | 82 | 89 | 76 | 38 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 419 |  |  |  | 8 | 57 | 57 | 55 | 93 | 82 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 303 |  | 4 |  | 13 | 42 | 29 | 34 | 77 | 60 | 34 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 292 | 13 | 8 | 5 | 35 | 51 | 21 | 21 | 25 | 60 | 29 | 7 | 17
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 301 | 13 | 21 | 11 | 71 | 43 | 5 |  | 4 | 35 | 47 | 32 | 19
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 313 | 8 | 31 | 23 | 74 | 45 | 1 |  | 1 | 13 | 60 | 46 | 11
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 300 | 12 | 38 | 42 | 45 | 19 |  |  |  |  | 37 | 64 | 43
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 210 | 26 | 27 | 52 | 25 | 2 |  |  |  |  | 17 | 26 | 35
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 290 | 52 | 21 | 80 | 21 | [5 empty] | 6 | 47 | 63
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 195 | 38 | 24 | 47 | 6 | [6 empty] | 46 | 34
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 164 | 45 | 34 | 38 | 2 | [6 empty] | 24 | 21
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 80 | 11 | 32 | 11 | [7 empty] | 6 | 20
22.5 | 20 to 25 | 277 | 106 | 47 | 26 |  |  |  |  | Reduction In Operating Hours AHU #4: 28; Reduction In Operating Hours AHU #5: 70; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 95 | 55 | 17 | 1 | [7 empty] | 1 | 21
17.5 | 15 to 20 | 178 | 81 | 55 | 6 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 52 | 29 | 17 | [8 empty] | 1 | 5
12.5 | 10 to 15 | 71 | 47 | 22 | [5 empty] | Reduction In Operating Hours AHU #5: 2; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 13 | 8 | 5
7.5 | 5 to 10 | 9 | 1 | 8 | [5 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10
2.5 | 0 to 5 | 4 |  | 4 | [5 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 |  | 1
-2.5 | -5 to 0 | 1 |  | 1 | [5 empty] | Reduction In Operating Hours AHU #7: -2.5
|  | 8760 | [15 empty] | 3650
AHU #2
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 100 | 200 | 200 | 1 | [5 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Saturday | 800 | 1300 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 800 | 1300 | 100
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [8 empty] | 8
[10 empty] | Reduction In Operating Hours AHU #1: 9 | [8 empty] | 9
[10 empty] | Reduction In Operating Hours AHU #1: 10 | [8 empty] | 10
[10 empty] | Reduction In Operating Hours AHU #1: 11 | [8 empty] | 11
| 100 | 200 | [7 empty] | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 0 | 100 | [7 empty] | 12
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 800 | 1300 | [7 empty] | Reduction In Operating Hours RTU # 1: 800 | 1300
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 2 | [6 empty] | 2 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 2 | [6 empty] | 2
92.5 | 90 to 95 | 2 | [6 empty] | 2 | Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 2 | [6 empty] | 2
87.5 | 85 to 90 | 6 | [5 empty] | 1 | 3 | Reduction In Operating Hours AHU #2: 2; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 6 | [5 empty] | 1 | 3 |  | 2
82.5 | 80 to 85 | 20 |  |  |  |  | 3 | 6 | 5 | Reduction In Operating Hours AHU #1: 4; Reduction In Operating Hours AHU #2: 2; Reduction In Operating Hours AHU #7: 82.5; Reduction In Operating Hours RTU # 1: 80 to 85 | 20 |  |  |  |  | 3 | 6 | 5 | 4 | 2
77.5 | 75 to 80 | 37 |  |  |  |  | 6 | 3 | 7 | 11 | 7 | 3 |  |  |  | 77.5 | 75 to 80 | 37 |  |  |  |  | 6 | 3 | 7 | 11 | 7 | 3
72.5 | 70 to 75 | 20 |  |  |  |  | 2 | 6 | 1 | 5 | 4 | 2 |  |  |  | 72.5 | 70 to 75 | 20 |  |  |  |  | 2 | 6 | 1 | 5 | 4 | 2
67.5 | 65 to 70 | 23 |  | 2 |  |  | 3 | 2 | 5 | Reduction In Operating Hours AHU #2: 9; Reduction In Operating Hours AHU #3: 2; Reduction In Operating Hours AHU #7: 67.5; Reduction In Operating Hours RTU # 1: 65 to 70 | 23 |  | 2 |  |  | 3 | 2 | 5 |  | 9 | 2
62.5 | 60 to 65 | 14 |  | 1 |  | 2 | 1 | 2 |  |  | 1 | 2 | 4 | 1 |  | 62.5 | 60 to 65 | 14 |  | 1 |  | 2 | 1 | 2 |  |  | 1 | 2 | 4 | 1
57.5 | 55 to 60 | 15 |  | 1 |  | 5 | 3 |  |  |  |  | 3 | 2 | 1 |  | 57.5 | 55 to 60 | 15 |  | 1 |  | 5 | 3 |  |  |  |  | 3 | 2 | 1
52.5 | 50 to 55 | 30 |  | 6 | 4 | 10 | 2 |  |  |  |  | 3 | 4 | 1 |  | 52.5 | 50 to 55 | 30 |  | 6 | 4 | 10 | 2 |  |  |  |  | 3 | 4 | 1
47.5 | 45 to 50 | 21 | 2 |  | 4 | 6 |  |  |  | Reduction In Operating Hours AHU #3: 3; Reduction In Operating Hours AHU #5: 6; Reduction In Operating Hours AHU #7: 47.5; Reduction In Operating Hours RTU # 1: 45 to 50 | 21 | 2 |  | 4 | 6 | [5 empty] | 3 |  | 6
42.5 | 40 to 45 | 24 | 8 |  | 5 | 2 | [5 empty] | 2 | 3 | 4 |  | 42.5 | 40 to 45 | 24 | 8 |  | 5 | 2 | [5 empty] | 2 | 3 | 4
37.5 | 35 to 40 | 11 |  | 1 | 4 |  |  |  |  | Reduction In Operating Hours AHU #4: 4; Reduction In Operating Hours AHU #5: 2; Reduction In Operating Hours AHU #7: 37.5; Reduction In Operating Hours RTU # 1: 35 to 40 | 11 |  | 1 | 4 | [7 empty] | 4 | 2
32.5 | 30 to 35 | 11 |  | 3 | 2 |  |  |  |  | Reduction In Operating Hours AHU #4: 3; Reduction In Operating Hours AHU #5: 3; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 11 |  | 3 | 2 | [7 empty] | 3 | 3
27.5 | 25 to 30 | 3 |  | 1 | 1 |  |  |  |  | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 3 |  | 1 | 1 | [8 empty] | 1
22.5 | 20 to 25 | 10 | 5 | [6 empty] | Reduction In Operating Hours AHU #5: 5; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 10 | 5 | [10 empty] | 5
17.5 | 15 to 20 | 6 | 2 | 3 | [5 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 6 | 2 | 3 | [9 empty] | 1
12.5 | 10 to 15 | 5 | 3 | 2 | [5 empty] | Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 5 | 3 | 2
7.5 | 5 to 10 | [8 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10
2.5 | 0 to 5 | [8 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5
|  | 260 | [15 empty] | 260
AHU #3
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | Reduction In Operating Hours AHU #1: 1; Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500
Tuesday | 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | Reduction In Operating Hours AHU #1: 3; Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500
Wednesday | 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | Reduction In Operating Hours AHU #1: 4; Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500
Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | Reduction In Operating Hours AHU #1: 5; Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500
Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | Reduction In Operating Hours AHU #1: 6; Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500
Saturday | 100 | 2400 | 5500 | 7 | 7 | 7 | 7 | 7 | 7 | Reduction In Operating Hours AHU #1: 7; Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | Reduction In Operating Hours AHU #1: 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | Reduction In Operating Hours AHU #1: 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | Reduction In Operating Hours AHU #1: 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 100 | 2500
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 100 | 2500
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 100 | 2500
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 100 | 2500
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | Reduction In Operating Hours AHU #1: 16; Reduction In Operating Hours RTU # 1: 100 | 2500
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | Reduction In Operating Hours AHU #1: 17; Reduction In Operating Hours RTU # 1: 100 | 2500
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | Reduction In Operating Hours AHU #1: 18; Reduction In Operating Hours RTU # 1: 100 | 2500
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | Reduction In Operating Hours AHU #1: 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | Reduction In Operating Hours AHU #1: 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | Reduction In Operating Hours AHU #1: 21 |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | Reduction In Operating Hours AHU #1: 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | Reduction In Operating Hours AHU #1: 23 |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | Reduction In Operating Hours AHU #1: 24 |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 2 | [6 empty] | 2
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 11 |  |  |  |  | 1 |  | 8 | 2
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 77 |  |  |  |  | 3 | 19 | 40 | 15
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 187 |  |  |  |  | 3 | 57 | 55 | 56 | 14 | 2
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 211 |  |  |  |  | 31 | 37 | 40 | 38 | 41 | 19 | 1 | 4
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 203 | 9 | 6 |  | 5 | 46 | 19 | 10 | 26 | 45 | 22 | 4 | 11
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 158 | 1 | 8 | 5 | 22 | 20 | 11 |  | 17 | 30 | 24 | 5 | 15
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 153 | 2 | 29 | 7 | 37 | 18 | 7 |  | 1 | 12 | 24 | 12 | 4
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 145 | 8 | 2 | 20 | 36 | 23 |  |  |  | 6 | 14 | 22 | 14
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 206 | 25 | 18 | 42 | 33 | 9 |  |  |  | 2 | 31 | 27 | 19
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 162 | 23 | 15 | 37 | 8 | 1 |  |  |  |  | 10 | 36 | 32
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 103 | 17 | 10 | 21 | 9 | [5 empty] | 8 | 21 | 17
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 79 | 19 | 21 | 15 | [6 empty] | 1 | 9 | 14
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 65 | 20 | 11 | 8 | [7 empty] | 10 | 16
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 39 | 19 | 10 | [8 empty] | 3 | 7
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 23 | 12 | 9 | [9 empty] | 2
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 1 |  | 1
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5
|  | 8760 | [15 empty] | 1825
AHU #4
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 400 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 287 | 110 | 68 | 23 | [7 empty] | 17 | 69
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 196 | 106 | 27 | 1 | [7 empty] | 7 | 55
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 214 | 144 | 8 | [9 empty] | 62
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 83 | 54 | [10 empty] | 29
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 10 | 9 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 5 | 5
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 8760
AHU #5
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Monday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Tuesday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Wednesday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Thursday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Friday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Saturday | 700 | 1900 | 2300 | 7 | 7 | 7 | 7 | 7 | 7 | Reduction In Operating Hours AHU #1: 7; Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 2200 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | Reduction In Operating Hours AHU #1: 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | Reduction In Operating Hours AHU #1: 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | Reduction In Operating Hours AHU #1: 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 700 | 1900 |  | 12 | 12 | 12 | 12 | 12 | 12 | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 700 | 1900 |  | 13 | 13 | 13 | 13 | 13 | 13 | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 700 | 1900 |  | 14 | 14 | 14 | 14 | 14 | 14 | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 700 | 1900 |  | 15 | 15 | 15 | 15 | 15 | 15 | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 700 | 1900 |  | 16 | 16 | 16 | 16 | 16 | 16 | Reduction In Operating Hours AHU #1: 16; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 700 | 1900 |  | 17 | 17 | 17 | 17 | 17 | 17 | Reduction In Operating Hours AHU #1: 17; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 700 | 1900 |  | 18 | 18 | 18 | 18 | 18 | 18 | Reduction In Operating Hours AHU #1: 18; Reduction In Operating Hours RTU # 1: 700 | 1800
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | Reduction In Operating Hours AHU #7: 102.5; Reduction In Operating Hours RTU # 1: 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 26 | [5 empty] | 8 | 18
92.5 | 90 to 95 | 70 | [5 empty] | 32 | 36 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 67 | [5 empty] | 31 | 34 | 2
87.5 | 85 to 90 | 184 |  |  |  |  | 7 | 71 | 61 | Reduction In Operating Hours AHU #1: 33; Reduction In Operating Hours AHU #2: 12; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 172 |  |  |  |  | 6 | 66 | 56 | 32 | 12
82.5 | 80 to 85 | 384 |  |  |  |  | 48 | 90 | 101 | 81 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 356 |  |  |  |  | 45 | 82 | 91 | 76 | 38 | 24
77.5 | 75 to 80 | 476 |  |  |  | 9 | 62 | 73 | 71 | 107 | 87 | 56 |  | 11 |  | 77.5 | 75 to 80 | 440 |  |  |  | 8 | 57 | 66 | 65 | 95 | 82 | 56 |  | 11
72.5 | 70 to 75 | 385 |  | 4 |  | 13 | 50 | 47 | 52 | 99 | 74 | 36 |  | 10 |  | 72.5 | 70 to 75 | 344 |  | 4 |  | 13 | 44 | 40 | 47 | 87 | 64 | 35 |  | 10
67.5 | 65 to 70 | 364 | 14 | 9 | 6 | 41 | 65 | 27 | 28 | 35 | 74 | 39 | 7 | 19 |  | 67.5 | 65 to 70 | 325 | 13 | 8 | 5 | 35 | 59 | 25 | 27 | 34 | 65 | 30 | 7 | 17
62.5 | 60 to 65 | 354 | 14 | 22 | 12 | 77 | 52 | 8 |  | 12 | 49 | 53 | 32 | 23 |  | 62.5 | 60 to 65 | 334 | 13 | 21 | 11 | 73 | 48 | 8 |  | 12 | 46 | 49 | 32 | 21
57.5 | 55 to 60 | 379 | 10 | 36 | 25 | 86 | 55 | 4 |  | 3 | 21 | 73 | 51 | 15 |  | 57.5 | 55 to 60 | 346 | 9 | 32 | 23 | 75 | 51 | 4 |  | 3 | 20 | 69 | 46 | 14
52.5 | 50 to 55 | 369 | 15 | 46 | 49 | 56 | 27 |  |  |  | 2 | 48 | 75 | 51 |  | 52.5 | 50 to 55 | 337 | 14 | 43 | 44 | 54 | 25 |  |  |  | 2 | 41 | 69 | 45
47.5 | 45 to 50 | 255 | 31 | 34 | 57 | 33 | 6 |  |  |  | 1 | 27 | 31 | 35 |  | 47.5 | 45 to 50 | 229 | 27 | 30 | 52 | 29 | 6 |  |  |  | 1 | 22 | 27 | 35
42.5 | 40 to 45 | 357 | 60 | 25 | 100 | 32 | [5 empty] | 11 | 56 | 73 |  | 42.5 | 40 to 45 | 328 | 56 | 23 | 90 | 31 | [5 empty] | 10 | 50 | 68
37.5 | 35 to 40 | 245 | 45 | 30 | 54 | 9 | [5 empty] | 3 | 57 | 47 |  | 37.5 | 35 to 40 | 227 | 42 | 28 | 51 | 8 | [5 empty] | 3 | 53 | 42
32.5 | 30 to 35 | 214 | 55 | 39 | 52 | 4 | [5 empty] | 1 | 34 | 29 |  | 32.5 | 30 to 35 | 193 | 48 | 36 | 48 | 4 | [5 empty] | 1 | 31 | 25
27.5 | 25 to 30 | 101 | 15 | 39 | 12 | [6 empty] | 1 | 11 | 23 |  | 27.5 | 25 to 30 | 93 | 15 | 35 | 12 | [6 empty] | 1 | 10 | 20
22.5 | 20 to 25 | 118 | 62 | 20 | 4 |  |  |  |  | Reduction In Operating Hours AHU #4: 4; Reduction In Operating Hours AHU #5: 28; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 108 | 58 | 18 | 4 | [7 empty] | 3 | 25
17.5 | 15 to 20 | 71 | 38 | 22 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 2; Reduction In Operating Hours AHU #5: 8; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 65 | 33 | 21 | 1 | [7 empty] | 2 | 8
12.5 | 10 to 15 | 19 | 12 | 7 | [5 empty] | Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 18 | 12 | 6
7.5 | 5 to 10 | 2 | 1 | 1 | [5 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 2 | 1 | 1
[10 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 |  | 1
[10 empty] | Reduction In Operating Hours AHU #7: -2.5; Reduction In Operating Hours RTU # 1: -5 to 0 | 1 |  | 1
|  | 4378 | [15 empty] | 4015
AHU #6
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 400 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 400
Friday | 0 | 100 | 400 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 400
Saturday | 800 | 1600 | 400 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 800 | 1600 | 400
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [8 empty] | 8
[10 empty] | Reduction In Operating Hours AHU #1: 9 | [8 empty] | 9
[10 empty] | Reduction In Operating Hours AHU #1: 10 | [8 empty] | 10
[10 empty] | Reduction In Operating Hours AHU #1: 11 | [8 empty] | 11
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 0 | 100 | [7 empty] | 12
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 0 | 100 | [7 empty] | 13
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 0 | 100 | [7 empty] | 14
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 0 | 100 | [7 empty] | 15
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 800 | 1600 | [7 empty] | Reduction In Operating Hours RTU # 1: 800 | 1600
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 3 | [6 empty] | 3 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 3 | [6 empty] | 3
92.5 | 90 to 95 | 5 | [5 empty] | 2 | 3 | Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 5 | [5 empty] | 2 | 3
87.5 | 85 to 90 | 20 | [5 empty] | 4 | 7 | Reduction In Operating Hours AHU #1: 4; Reduction In Operating Hours AHU #2: 5; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 20 | [5 empty] | 4 | 7 | 4 | 5
82.5 | 80 to 85 | 39 |  |  |  |  | 6 | 10 | 9 | Reduction In Operating Hours AHU #1: 9; Reduction In Operating Hours AHU #2: 5; Reduction In Operating Hours AHU #7: 82.5; Reduction In Operating Hours RTU # 1: 80 to 85 | 39 |  |  |  |  | 6 | 10 | 9 | 9 | 5
77.5 | 75 to 80 | 48 |  |  |  |  | 9 | 4 | 8 | 11 | 7 | 9 |  |  |  | 77.5 | 75 to 80 | 48 |  |  |  |  | 9 | 4 | 8 | 11 | 7 | 9
72.5 | 70 to 75 | 41 |  | 3 |  |  | 5 | 8 | 2 | 8 | 13 | 2 |  |  |  | 72.5 | 70 to 75 | 41 |  | 3 |  |  | 5 | 8 | 2 | 8 | 13 | 2
67.5 | 65 to 70 | 30 |  | 2 |  | 2 | 3 | 2 | 8 |  | 9 | 2 | 2 |  |  | 67.5 | 65 to 70 | 30 |  | 2 |  | 2 | 3 | 2 | 8 |  | 9 | 2 | 2
62.5 | 60 to 65 | 21 |  | 1 |  | 5 | 1 | 2 |  |  | 1 | 2 | 5 | 4 |  | 62.5 | 60 to 65 | 21 |  | 1 |  | 5 | 1 | 2 |  |  | 1 | 2 | 5 | 4
57.5 | 55 to 60 | 39 |  | 2 | 3 | 14 | 6 |  |  |  |  | 6 | 5 | 3 |  | 57.5 | 55 to 60 | 39 |  | 2 | 3 | 14 | 6 |  |  |  |  | 6 | 5 | 3
52.5 | 50 to 55 | 42 |  | 8 | 7 | 11 | 2 |  |  |  |  | 6 | 4 | 4 |  | 52.5 | 50 to 55 | 42 |  | 8 | 7 | 11 | 2 |  |  |  |  | 6 | 4 | 4
47.5 | 45 to 50 | 23 | 3 |  | 4 | 6 |  |  |  | Reduction In Operating Hours AHU #3: 3; Reduction In Operating Hours AHU #5: 7; Reduction In Operating Hours AHU #7: 47.5; Reduction In Operating Hours RTU # 1: 45 to 50 | 23 | 3 |  | 4 | 6 | [5 empty] | 3 |  | 7
42.5 | 40 to 45 | 37 | 13 |  | 10 | 2 | [5 empty] | 2 | 6 | 4 |  | 42.5 | 40 to 45 | 37 | 13 |  | 10 | 2 | [5 empty] | 2 | 6 | 4
37.5 | 35 to 40 | 18 |  | 4 | 5 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 2; Reduction In Operating Hours AHU #7: 37.5; Reduction In Operating Hours RTU # 1: 35 to 40 | 18 |  | 4 | 5 | [7 empty] | 7 | 2
32.5 | 30 to 35 | 14 |  | 3 | 2 |  |  |  |  | Reduction In Operating Hours AHU #4: 3; Reduction In Operating Hours AHU #5: 6; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 14 |  | 3 | 2 | [7 empty] | 3 | 6
27.5 | 25 to 30 | 6 |  | 1 | 1 |  |  |  |  | Reduction In Operating Hours AHU #5: 4; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 6 |  | 1 | 1 | [8 empty] | 4
22.5 | 20 to 25 | 16 | 11 | [6 empty] | Reduction In Operating Hours AHU #5: 5; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 16 | 11 | [10 empty] | 5
17.5 | 15 to 20 | 9 | 2 | 6 | [5 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 9 | 2 | 6 | [9 empty] | 1
12.5 | 10 to 15 | 5 | 3 | 2 | [5 empty] | Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 5 | 3 | 2
7.5 | 5 to 10 | [8 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10
2.5 | 0 to 5 | [8 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5
|  | 416 | [15 empty] | 416
AHU #7
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Monday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Tuesday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Wednesday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Thursday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Friday | 700 | 1900 | 1900 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 1800
Saturday | 700 | 1900 | 2300 | 7 | 7 | 7 | 7 | 7 | 7 | Reduction In Operating Hours AHU #1: 7; Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 700 | 1800 | 2200 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | Reduction In Operating Hours AHU #1: 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | Reduction In Operating Hours AHU #1: 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | Reduction In Operating Hours AHU #1: 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 700 | 1900 |  | 12 | 12 | 12 | 12 | 12 | 12 | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 700 | 1900 |  | 13 | 13 | 13 | 13 | 13 | 13 | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 700 | 1900 |  | 14 | 14 | 14 | 14 | 14 | 14 | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 700 | 1900 |  | 15 | 15 | 15 | 15 | 15 | 15 | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 700 | 1900 |  | 16 | 16 | 16 | 16 | 16 | 16 | Reduction In Operating Hours AHU #1: 16; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 700 | 1900 |  | 17 | 17 | 17 | 17 | 17 | 17 | Reduction In Operating Hours AHU #1: 17; Reduction In Operating Hours RTU # 1: 700 | 1800 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 700 | 1900 |  | 18 | 18 | 18 | 18 | 18 | 18 | Reduction In Operating Hours AHU #1: 18; Reduction In Operating Hours RTU # 1: 700 | 1800
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | Reduction In Operating Hours AHU #7: 102.5; Reduction In Operating Hours RTU # 1: 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 26 | [5 empty] | 8 | 18
92.5 | 90 to 95 | 70 | [5 empty] | 32 | 36 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 67 | [5 empty] | 31 | 34 | 2
87.5 | 85 to 90 | 184 |  |  |  |  | 7 | 71 | 61 | Reduction In Operating Hours AHU #1: 33; Reduction In Operating Hours AHU #2: 12; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 172 |  |  |  |  | 6 | 66 | 56 | 32 | 12
82.5 | 80 to 85 | 384 |  |  |  |  | 48 | 90 | 101 | 81 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 356 |  |  |  |  | 45 | 82 | 91 | 76 | 38 | 24
77.5 | 75 to 80 | 476 |  |  |  | 9 | 62 | 73 | 71 | 107 | 87 | 56 |  | 11 |  | 77.5 | 75 to 80 | 440 |  |  |  | 8 | 57 | 66 | 65 | 95 | 82 | 56 |  | 11
72.5 | 70 to 75 | 385 |  | 4 |  | 13 | 50 | 47 | 52 | 99 | 74 | 36 |  | 10 |  | 72.5 | 70 to 75 | 344 |  | 4 |  | 13 | 44 | 40 | 47 | 87 | 64 | 35 |  | 10
67.5 | 65 to 70 | 364 | 14 | 9 | 6 | 41 | 65 | 27 | 28 | 35 | 74 | 39 | 7 | 19 |  | 67.5 | 65 to 70 | 325 | 13 | 8 | 5 | 35 | 59 | 25 | 27 | 34 | 65 | 30 | 7 | 17
62.5 | 60 to 65 | 354 | 14 | 22 | 12 | 77 | 52 | 8 |  | 12 | 49 | 53 | 32 | 23 |  | 62.5 | 60 to 65 | 334 | 13 | 21 | 11 | 73 | 48 | 8 |  | 12 | 46 | 49 | 32 | 21
57.5 | 55 to 60 | 379 | 10 | 36 | 25 | 86 | 55 | 4 |  | 3 | 21 | 73 | 51 | 15 |  | 57.5 | 55 to 60 | 346 | 9 | 32 | 23 | 75 | 51 | 4 |  | 3 | 20 | 69 | 46 | 14
52.5 | 50 to 55 | 369 | 15 | 46 | 49 | 56 | 27 |  |  |  | 2 | 48 | 75 | 51 |  | 52.5 | 50 to 55 | 337 | 14 | 43 | 44 | 54 | 25 |  |  |  | 2 | 41 | 69 | 45
47.5 | 45 to 50 | 255 | 31 | 34 | 57 | 33 | 6 |  |  |  | 1 | 27 | 31 | 35 |  | 47.5 | 45 to 50 | 229 | 27 | 30 | 52 | 29 | 6 |  |  |  | 1 | 22 | 27 | 35
42.5 | 40 to 45 | 357 | 60 | 25 | 100 | 32 | [5 empty] | 11 | 56 | 73 |  | 42.5 | 40 to 45 | 328 | 56 | 23 | 90 | 31 | [5 empty] | 10 | 50 | 68
37.5 | 35 to 40 | 245 | 45 | 30 | 54 | 9 | [5 empty] | 3 | 57 | 47 |  | 37.5 | 35 to 40 | 227 | 42 | 28 | 51 | 8 | [5 empty] | 3 | 53 | 42
32.5 | 30 to 35 | 214 | 55 | 39 | 52 | 4 | [5 empty] | 1 | 34 | 29 |  | 32.5 | 30 to 35 | 193 | 48 | 36 | 48 | 4 | [5 empty] | 1 | 31 | 25
27.5 | 25 to 30 | 101 | 15 | 39 | 12 | [6 empty] | 1 | 11 | 23 |  | 27.5 | 25 to 30 | 93 | 15 | 35 | 12 | [6 empty] | 1 | 10 | 20
22.5 | 20 to 25 | 118 | 62 | 20 | 4 |  |  |  |  | Reduction In Operating Hours AHU #4: 4; Reduction In Operating Hours AHU #5: 28; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 108 | 58 | 18 | 4 | [7 empty] | 3 | 25
17.5 | 15 to 20 | 71 | 38 | 22 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 2; Reduction In Operating Hours AHU #5: 8; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 65 | 33 | 21 | 1 | [7 empty] | 2 | 8
12.5 | 10 to 15 | 19 | 12 | 7 | [5 empty] | Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 18 | 12 | 6
7.5 | 5 to 10 | 2 | 1 | 1 | [5 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 2 | 1 | 1
[10 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 |  | 1
[10 empty] | Reduction In Operating Hours AHU #7: -2.5; Reduction In Operating Hours RTU # 1: -5 to 0 | 1 |  | 1
|  | 4378 | [15 empty] | 4015
RTU # 1
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | Reduction In Operating Hours AHU #1: 1; Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | Reduction In Operating Hours AHU #1: 3; Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | Reduction In Operating Hours AHU #1: 4; Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | Reduction In Operating Hours AHU #1: 5; Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | Reduction In Operating Hours AHU #1: 6; Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | Reduction In Operating Hours AHU #1: 7; Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | Reduction In Operating Hours AHU #1: 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | Reduction In Operating Hours AHU #1: 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | Reduction In Operating Hours AHU #1: 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | Reduction In Operating Hours AHU #1: 16; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | Reduction In Operating Hours AHU #1: 17; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | Reduction In Operating Hours AHU #1: 18; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | Reduction In Operating Hours AHU #1: 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | Reduction In Operating Hours AHU #1: 20 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | Reduction In Operating Hours AHU #1: 21 |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | Reduction In Operating Hours AHU #1: 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | Reduction In Operating Hours AHU #1: 23 |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | Reduction In Operating Hours AHU #1: 24 |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | Reduction In Operating Hours AHU #7: 102.5; Reduction In Operating Hours RTU # 1: 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | Reduction In Operating Hours AHU #1: 33; Reduction In Operating Hours AHU #2: 12; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47
22.5 | 20 to 25 | 277 | 106 | 47 | 26 |  |  |  |  | Reduction In Operating Hours AHU #4: 28; Reduction In Operating Hours AHU #5: 70; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70
17.5 | 15 to 20 | 178 | 81 | 55 | 6 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29
12.5 | 10 to 15 | 71 | 47 | 22 | [5 empty] | Reduction In Operating Hours AHU #5: 2; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 71 | 47 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [5 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 9 | 1 | 8
2.5 | 0 to 5 | 4 |  | 4 | [5 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 4 |  | 4
-2.5 | -5 to 0 | 1 |  | 1 | [5 empty] | Reduction In Operating Hours AHU #7: -2.5; Reduction In Operating Hours RTU # 1: -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 8760
0
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | Reduction In Operating Hours AHU #1: 1; Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | Reduction In Operating Hours AHU #1: 3; Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | Reduction In Operating Hours AHU #1: 4; Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | Reduction In Operating Hours AHU #1: 5; Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | Reduction In Operating Hours AHU #1: 6; Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | Reduction In Operating Hours AHU #1: 7; Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 3000 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | Reduction In Operating Hours AHU #1: 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | Reduction In Operating Hours AHU #1: 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | Reduction In Operating Hours AHU #1: 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | Reduction In Operating Hours AHU #1: 16; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | Reduction In Operating Hours AHU #1: 17; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | Reduction In Operating Hours AHU #1: 18; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | Reduction In Operating Hours AHU #1: 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | Reduction In Operating Hours AHU #1: 20 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | Reduction In Operating Hours AHU #1: 21 |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | Reduction In Operating Hours AHU #1: 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | Reduction In Operating Hours AHU #1: 23 |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | Reduction In Operating Hours AHU #1: 24 |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | Reduction In Operating Hours AHU #7: 102.5; Reduction In Operating Hours RTU # 1: 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | Reduction In Operating Hours AHU #1: 33; Reduction In Operating Hours AHU #2: 12; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47
22.5 | 20 to 25 | 277 | 106 | 47 | 26 |  |  |  |  | Reduction In Operating Hours AHU #4: 28; Reduction In Operating Hours AHU #5: 70; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70
17.5 | 15 to 20 | 178 | 81 | 55 | 6 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29
12.5 | 10 to 15 | 71 | 47 | 22 | [5 empty] | Reduction In Operating Hours AHU #5: 2; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 71 | 47 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [5 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 9 | 1 | 8
2.5 | 0 to 5 | 4 |  | 4 | [5 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 4 |  | 4
-2.5 | -5 to 0 | 1 |  | 1 | [5 empty] | Reduction In Operating Hours AHU #7: -2.5; Reduction In Operating Hours RTU # 1: -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 8760
0
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | Reduction In Operating Hours AHU #1: 1; Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Monday | 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Tuesday | 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | Reduction In Operating Hours AHU #1: 3; Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Wednesday | 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | Reduction In Operating Hours AHU #1: 4; Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Thursday | 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | Reduction In Operating Hours AHU #1: 5; Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Friday | 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | Reduction In Operating Hours AHU #1: 6; Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Saturday | 100 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | Reduction In Operating Hours AHU #1: 7; Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 100 | 2400 | 2500 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | Reduction In Operating Hours AHU #1: 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | Reduction In Operating Hours AHU #1: 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | Reduction In Operating Hours AHU #1: 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11
| 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13
| 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14
| 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | Reduction In Operating Hours AHU #1: 16; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | Reduction In Operating Hours AHU #1: 17; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17
| 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | Reduction In Operating Hours AHU #1: 18; Reduction In Operating Hours RTU # 1: 100 | 2500 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18
|  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | Reduction In Operating Hours AHU #1: 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | Reduction In Operating Hours AHU #1: 20 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | Reduction In Operating Hours AHU #1: 21 |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | Reduction In Operating Hours AHU #1: 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | 23 | 23 | 23 | 23 | 23 | 23 | Reduction In Operating Hours AHU #1: 23 |  |  | 23 | 23 | 23 | 23 | 23 | 23 | 23
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | Reduction In Operating Hours AHU #1: 24 |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
102.5 | 100 to 105 | 3 | [6 empty] | 3 | Reduction In Operating Hours AHU #7: 102.5; Reduction In Operating Hours RTU # 1: 100 to 105 | 3 | [6 empty] | 3
97.5 | 95 to 100 | 28 | [5 empty] | 8 | 20 | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 28 | [5 empty] | 8 | 20
92.5 | 90 to 95 | 72 | [5 empty] | 32 | 38 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 72 | [5 empty] | 32 | 38 | 2
87.5 | 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | Reduction In Operating Hours AHU #1: 33; Reduction In Operating Hours AHU #2: 12; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 192 |  |  |  |  | 7 | 72 | 68 | 33 | 12
82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24 |  |  |  | 82.5 | 80 to 85 | 420 |  |  |  |  | 51 | 97 | 121 | 87 | 40 | 24
77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11 |  | 77.5 | 75 to 80 | 649 |  |  |  | 9 | 68 | 114 | 159 | 139 | 93 | 56 |  | 11
72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10 |  | 72.5 | 70 to 75 | 819 |  | 4 |  | 13 | 70 | 178 | 180 | 219 | 102 | 43 |  | 10
67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31 |  | 67.5 | 65 to 70 | 873 | 18 | 10 | 6 | 42 | 116 | 124 | 126 | 137 | 177 | 76 | 10 | 31
62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46 |  | 62.5 | 60 to 65 | 782 | 30 | 29 | 14 | 97 | 153 | 50 | 29 | 68 | 134 | 96 | 36 | 46
57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50 |  | 57.5 | 55 to 60 | 768 | 14 | 60 | 36 | 141 | 112 | 19 |  | 42 | 100 | 128 | 66 | 50
52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70 |  | 52.5 | 50 to 55 | 795 | 19 | 110 | 68 | 125 | 81 | 23 |  | 17 | 42 | 124 | 116 | 70
47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62 |  | 47.5 | 45 to 50 | 551 | 53 | 50 | 88 | 105 | 47 | 2 |  |  | 11 | 56 | 77 | 62
42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116 |  | 42.5 | 40 to 45 | 858 | 122 | 64 | 213 | 108 | 31 | 1 |  |  | 9 | 87 | 107 | 116
37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120 |  | 37.5 | 35 to 40 | 651 | 92 | 65 | 131 | 60 | 8 |  |  |  |  | 33 | 142 | 120
32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80 |  | 32.5 | 30 to 35 | 476 | 98 | 62 | 120 | 16 | [5 empty] | 17 | 83 | 80
27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47 |  | 27.5 | 25 to 30 | 283 | 63 | 81 | 36 | 4 | [5 empty] | 4 | 48 | 47
22.5 | 20 to 25 | 277 | 106 | 47 | 26 |  |  |  |  | Reduction In Operating Hours AHU #4: 28; Reduction In Operating Hours AHU #5: 70; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 277 | 106 | 47 | 26 | [7 empty] | 28 | 70
17.5 | 15 to 20 | 178 | 81 | 55 | 6 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 178 | 81 | 55 | 6 | [7 empty] | 7 | 29
12.5 | 10 to 15 | 71 | 47 | 22 | [5 empty] | Reduction In Operating Hours AHU #5: 2; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 71 | 47 | 22 | [9 empty] | 2
7.5 | 5 to 10 | 9 | 1 | 8 | [5 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 9 | 1 | 8
2.5 | 0 to 5 | 4 |  | 4 | [5 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 4 |  | 4
-2.5 | -5 to 0 | 1 |  | 1 | [5 empty] | Reduction In Operating Hours AHU #7: -2.5; Reduction In Operating Hours RTU # 1: -5 to 0 | 1 |  | 1
|  | 8760 | [15 empty] | 8760
0
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 287 | 110 | 68 | 23 | [7 empty] | 17 | 69
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 196 | 106 | 27 | 1 | [7 empty] | 7 | 55
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 214 | 144 | 8 | [9 empty] | 62
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 83 | 54 | [10 empty] | 29
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 10 | 9 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 5 | 5
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 8760
0
|  |  |  | EXISTING BIN HOURS | [15 empty] | PROPOSED BIN HOURS | bar: Reduction In Operating Hours AHU #1 to Reduction In Operating Hours AHU #5; Reduction In Operating Hours AHU #7 to Reduction In Operating Hours RTU # 1
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 287 | 110 | 68 | 23 | [7 empty] | 17 | 69
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 196 | 106 | 27 | 1 | [7 empty] | 7 | 55
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 214 | 144 | 8 | [9 empty] | 62
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 83 | 54 | [10 empty] | 29
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 10 | 9 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 5 | 5
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 8760
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 287 | 110 | 68 | 23 | [7 empty] | 17 | 69
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 196 | 106 | 27 | 1 | [7 empty] | 7 | 55
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 214 | 144 | 8 | [9 empty] | 62
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 83 | 54 | [10 empty] | 29
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 10 | 9 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 5 | 5
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 8760
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 287 | 110 | 68 | 23 | [7 empty] | 17 | 69
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 196 | 106 | 27 | 1 | [7 empty] | 7 | 55
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 214 | 144 | 8 | [9 empty] | 62
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 83 | 54 | [10 empty] | 29
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 10 | 9 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 5 | 5
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 8760
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 287 | 110 | 68 | 23 | [7 empty] | 17 | 69
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 196 | 106 | 27 | 1 | [7 empty] | 7 | 55
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 214 | 144 | 8 | [9 empty] | 62
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 83 | 54 | [10 empty] | 29
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 10 | 9 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 5 | 5
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 8760
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 287 | 110 | 68 | 23 | [7 empty] | 17 | 69
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 196 | 106 | 27 | 1 | [7 empty] | 7 | 55
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 214 | 144 | 8 | [9 empty] | 62
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 83 | 54 | [10 empty] | 29
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 10 | 9 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 5 | 5
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 8760
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 600 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 600
Saturday | 0 | 100 | 5500 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 5500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 800 | 1600 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #1: 8; Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
9
10
11
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 12; Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 13; Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 14; Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours AHU #1: 15; Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 800 | 1600 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665
0
EXISTING OPERATING HOURS | [9 empty] | Reduction In Operating Hours AHU #7: PROPOSED OPERATING HOURS
EXISTING HVAC SCHEDULE |  |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec | [5 empty] | Reduction In Operating Hours AHU #7: PROPOSED HVAC SCHEDULE |  |  | Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
| Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Reduction In Operating Hours AHU #1: Sat; Reduction In Operating Hours RTU # 1: Start | Stop |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat
Sunday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Sunday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Monday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Monday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Tuesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Tuesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Wednesday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Wednesday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Thursday | 0 | 100 | 100 | [6 empty] | Reduction In Operating Hours AHU #7: Thursday; Reduction In Operating Hours RTU # 1: 0 | 100 | 100
Friday | 0 | 100 | 10800 | [6 empty] | Reduction In Operating Hours AHU #7: Friday; Reduction In Operating Hours RTU # 1: 0 | 100 | 10100
Saturday | 0 | 100 | 15800 | [6 empty] | Reduction In Operating Hours AHU #7: Saturday; Reduction In Operating Hours RTU # 1: 0 | 100 | 13500
Table above is the actual schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment | [9 empty] | Reduction In Operating Hours AHU #7: Table above is the proposed schedule of HVAC start and stop times. Proposed bin hours to right represent total occupied hours of the HVAC equiptment
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
| 0 | 100 | [7 empty] | Reduction In Operating Hours RTU # 1: 0 | 100
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  |  |  | Total | January | February | March | April | May | June | July | August | September | October | November | December
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs |  | Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs
97.5 | 95 to 100 | 5 | [5 empty] | 5 |  | Reduction In Operating Hours AHU #7: 97.5; Reduction In Operating Hours RTU # 1: 95 to 100 | 5 | [5 empty] | 5
92.5 | 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | Reduction In Operating Hours AHU #1: 2; Reduction In Operating Hours AHU #7: 92.5; Reduction In Operating Hours RTU # 1: 90 to 95 | 40 |  |  |  |  | 6 | 14 | 18 | 2
87.5 | 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | Reduction In Operating Hours AHU #1: 28; Reduction In Operating Hours AHU #2: 26; Reduction In Operating Hours AHU #7: 87.5; Reduction In Operating Hours RTU # 1: 85 to 90 | 229 |  |  |  |  | 46 | 74 | 55 | 28 | 26
82.5 | 80 to 85 | 435 |  |  |  | 20 | 63 | 94 | 120 | 81 | 42 | 14 | 1 |  |  | 82.5 | 80 to 85 | 431 |  |  |  | 20 | 63 | 90 | 120 | 81 | 42 | 14 | 1
77.5 | 75 to 80 | 713 |  |  | 1 | 42 | 64 | 122 | 164 | 164 | 94 | 37 | 13 | 12 |  | 77.5 | 75 to 80 | 686 |  |  | 1 | 42 | 64 | 112 | 157 | 154 | 94 | 37 | 13 | 12
72.5 | 70 to 75 | 775 |  |  | 21 | 40 | 68 | 134 | 139 | 154 | 128 | 46 | 34 | 11 |  | 72.5 | 70 to 75 | 705 |  |  | 21 | 40 | 60 | 112 | 115 | 145 | 121 | 46 | 34 | 11
67.5 | 65 to 70 | 1091 | 7 | 3 | 43 | 96 | 131 | 127 | 175 | 174 | 179 | 87 | 39 | 30 |  | 67.5 | 65 to 70 | 946 | 7 | 3 | 43 | 95 | 113 | 100 | 137 | 141 | 151 | 87 | 39 | 30
62.5 | 60 to 65 | 1039 | 37 | 5 | 52 | 134 | 156 | 83 | 57 | 118 | 126 | 154 | 61 | 56 |  | 62.5 | 60 to 65 | 891 | 34 | 5 | 52 | 118 | 142 | 71 | 37 | 81 | 103 | 142 | 56 | 50
57.5 | 55 to 60 | 894 | 20 | 54 | 67 | 123 | 154 | 54 | 16 | 21 | 92 | 115 | 101 | 77 |  | 57.5 | 55 to 60 | 752 | 18 | 54 | 59 | 108 | 120 | 44 | 12 | 17 | 70 | 100 | 87 | 63
52.5 | 50 to 55 | 759 | 52 | 102 | 109 | 108 | 55 | 10 |  | 2 | 27 | 95 | 140 | 59 |  | 52.5 | 50 to 55 | 654 | 51 | 100 | 94 | 88 | 36 | 8 |  | 2 | 18 | 75 | 128 | 54
47.5 | 45 to 50 | 640 | 28 | 107 | 132 | 90 | 1 | 3 |  |  | 6 | 72 | 137 | 64 |  | 47.5 | 45 to 50 | 554 | 24 | 93 | 121 | 71 | 1 |  |  |  | 5 | 60 | 118 | 61
42.5 | 40 to 45 | 671 | 57 | 157 | 150 | 50 | [5 empty] | 77 | 89 | 91 |  | 42.5 | 40 to 45 | 535 | 47 | 134 | 122 | 35 | [5 empty] | 53 | 66 | 78
37.5 | 35 to 40 | 673 | 114 | 141 | 145 | 17 | [5 empty] | 47 | 81 | 128 |  | 37.5 | 35 to 40 | 581 | 108 | 121 | 120 | 13 | [5 empty] | 37 | 70 | 112
32.5 | 30 to 35 | 287 | 110 | 68 | 23 |  |  |  |  | Reduction In Operating Hours AHU #4: 17; Reduction In Operating Hours AHU #5: 69; Reduction In Operating Hours AHU #7: 32.5; Reduction In Operating Hours RTU # 1: 30 to 35 | 231 | 94 | 52 | 17 | [7 empty] | 11 | 57
27.5 | 25 to 30 | 196 | 106 | 27 | 1 |  |  |  |  | Reduction In Operating Hours AHU #4: 7; Reduction In Operating Hours AHU #5: 55; Reduction In Operating Hours AHU #7: 27.5; Reduction In Operating Hours RTU # 1: 25 to 30 | 167 | 92 | 18 | 1 | [7 empty] | 7 | 49
22.5 | 20 to 25 | 214 | 144 | 8 | [5 empty] | Reduction In Operating Hours AHU #5: 62; Reduction In Operating Hours AHU #7: 22.5; Reduction In Operating Hours RTU # 1: 20 to 25 | 173 | 117 | 8 | [9 empty] | 48
17.5 | 15 to 20 | 83 | 54 | [6 empty] | Reduction In Operating Hours AHU #5: 29; Reduction In Operating Hours AHU #7: 17.5; Reduction In Operating Hours RTU # 1: 15 to 20 | 72 | 47 | [10 empty] | 25
12.5 | 10 to 15 | 10 | 9 | [6 empty] | Reduction In Operating Hours AHU #5: 1; Reduction In Operating Hours AHU #7: 12.5; Reduction In Operating Hours RTU # 1: 10 to 15 | 9 | 8 | [10 empty] | 1
7.5 | 5 to 10 | 5 | 5 | [6 empty] | Reduction In Operating Hours AHU #7: 7.5; Reduction In Operating Hours RTU # 1: 5 to 10 | 3 | 3
2.5 | 0 to 5 | 1 | 1 | [6 empty] | Reduction In Operating Hours AHU #7: 2.5; Reduction In Operating Hours RTU # 1: 0 to 5 | 1 | 1
|  | 8760 | [15 empty] | 7665